“TECHNICAL SPECIFICATION FOR EVALUATION, SUPPLY AND TESTING”

S.T.V.F.C. 15AA300

WELDED STEEL PIPES,

FOR METHANE GAS PIPELINES

| Compiled by | APT-ATECH-NORM | MARELLA MANUELE |
| --- | --- | --- |
|  | APT-ATECH-NORM | NORDIO IVANO |
| Checked by | APT-ATECH-NORM | CIMINO SALVATORE |
| Checked by | PROMA/CMMAT | FASSINO SILVIO |
| Checked by | PROMA-MATMA | SCOTTO ENRICO |
| Checked by | BDT | AMBROSI LEONARDO |
| Checked by | HSEQ | LIMONTA AGOSTINO MASSIMO |
| Approved by | APT-ATECH | GHIBAUDO CLAUDIO |

SUMMARY

1	PRELIMINARY INFORMATION	4

1.1	Cancels and replaces	4

1.2	Reason for issue	4

1.3	Company departments mentioned in the document	4

2	PURPOSE AND FIELD OF APPLICATION	4

2.1	Purpose	4

2.2	Field of application	4

3	SPECIFICATIONS	4

4	PRESSURE RANGE	6

5	MATERIALS	6

5.1	Commercial gas pipe (for use at pressures of 0.04  MOP  0.5 bar) welded, with threaded ends, galvanised	6

5.1.1	Metallurgical characteristics of the raw pipe	6

5.1.2	Minimum dimensions and masses	6

5.1.3	Manufacturing process	7

5.1.4	Weld bead	7

5.1.5	Pipe end finish	7

5.1.6	Pipe length	7

5.1.7	Pipe marking	7

5.1.8	Protective coating	7

5.1.8.1	Coating	7

5.1.8.2	Coating marking	7

5.1.9	Supply and Testing	7

5.1.9.1	Production checks and tests	7

5.1.9.2	Inspection documents	8

5.2	PSL 1 Grade L210 pipe (for use at pressures of MOP  12 bar) with smooth ends and PE external coating	8

5.2.1	Metallurgical characteristics	8

5.2.2	Minimum dimensions and masses of pipes and coating	9

5.2.3	Manufacturing process	9

5.2.4	Pipe end finish	10

5.2.5	Pipe length	10

5.2.6	Pipe marking	10

5.2.7	External polyethylene coating applied by extrusion	11

5.2.7.1	Coating	11

5.2.7.2	Coating marking	11

5.2.8	Supply and Testing	11

5.2.8.1	Production checks and tests	11

5.2.8.2	Inspection documents	12

5.3	PSL 1 Grade L210 pipe (for use at pressures of MOP  12 bar) with smooth ends, raw	13

5.3.1	Metallurgical characteristics	13

5.3.2	Dimensions and masses minimums of tubes	13

5.3.3	Manufacturing process	13

5.3.4	Pipe end finish	14

5.3.5	Pipe length	14

5.3.6	Pipe marking	14

5.3.7	Supply and Testing	14

5.4	PSL 2 Grade L360N pipe (for use at pressures of 12  MOP  75 bar) with smooth ends and PE external coating	14

5.4.1	Metallurgical characteristics	14

5.4.2	Minimum dimensions and masses of pipes and coating	15

5.4.2.1	PSL 2 Grade L245N pipe (for use at pressures of 12  MOP ≤ 24 bar) - Metallurgical characteristics	15

5.4.2.2	PSL 2 Grade L245N pipe (for use at pressures of 12  MOP  24 bar) - Minimum dimensions and masses of pipe and coating	16

5.4.3	Manufacturing process	16

5.4.4	Pipe end finish	16

5.4.5	Pipe length	16

5.4.6	Pipe marking	16

5.4.7	External polyethylene coating applied by extrusion	17

5.4.8	Supply and Testing	17

5.4.8.1	Production checks and tests	17

5.4.8.2	Inspection documents	17

6	DOCUMENTATION FOR “THE APPROVAL FOR COMPANY USE PROCESS”	17

7	TESTS AND INSPECTIONS	18

8	REFERENCE STANDARDS	18

9	APPENDICES	19

# PRELIMINARY INFORMATION

The steel pipes defined in this Technical Specification for Evaluation, Supply and Testing (Italian acronym S.T.V.F.C.) must comply with the current reference standards and the construction and technical requirements of the Decrees of 16.04.2008 and 17.04.2008.

## Cancels and replaces

- S.T.V. no. 15AA300 ed. 1 of 15 June 2017.

## Reason for issue

This technical specification was issued to ensure compliance with industry standards and UNI 9034:2022, which cancels and replaces UNI 9034:2020. The update also adopts the new coated and coated pipe diameters DN 65, (2.5") and DN 125 (5").

## Company departments mentioned in the document

PROMA-CMMAT = Category Manager Materials

# PURPOSE AND FIELD OF APPLICATION

## Purpose

In accordance with the UNI EN 10255, API 5L (UNI EN ISO 3183 where applicable) and UNI EN 10220 standards, this technical specification defines the minimum requirements for the welded unalloyed steel pipes required by ITALGAS.

In particular, it specifies:

- The metallurgical characteristics of the steel from which welded pipes for natural gas distribution must be made;

- The dimensions of the pipes;

- The manufacturing process;

- The types of checks and test methods that the Supplier must guarantee ITALGAS for pipe supplies.

## Field of application

This technical specification applies:

- Whenever material covered by this specification must be authorised for company use, whether produced by a new potential Supplier or by an existing one;

- For the supply of welded steel pipes with nominal diameters up to DN 600 (24") conforming to APIStandard 5L (UNI EN ISO 3183 where applicable);

- For the supply of threaded pipes up to DN 80 (3") according to UNI EN 10255.

# SPECIFICATIONS

- This technical specification must be understood as an integral part of the "ITALGAS SUPPLIER EVALUATION AND QUALIFICATION SYSTEM";

- It is the Supplier's responsibility () to ensure that the products supplied fully comply with the provisions of this technical specification and the applicable standards;

- It is the Supplier's responsibility, during the product design, production and inspection process, to check that the finished products do not have any construction faults (e.g. sharp edges) that could endanger the health and safety of the Client's workers;

- For all technical and operational aspects that conflict with or are not mentioned in this technical specification, but nevertheless pertain to the design, execution, maintenance and use of the products themselves, it is the Supplier's responsibility to refer to the regulations in force;

- Any tests carried out on the materials do not in any case reduce the Supplier's liability.

# PRESSURE RANGE

The pressure range in which the steel pipes that are the subject of this technical specification are operated is shown in Table 1 below.

Table 1 - Pressure range

| Unalloyed welded steel tube |  | PRESSURE RANGE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Reference in the S.T.V. |  | B.P. | M.P.A. | M.P.B. | M.P.C. | A.P. |  |
| Prod. | Type | ≤ 0.04 bar | 0.04< P≤0.5 bar | 0.5 < P ≤ 5 bar | 5 < P ≤ 12 bar | 12 < P ≤ 24 bar | 24 < P ≤ 75 bar |
| 5.1 | Commercial, welded, threaded ends, galvanised. UNI EN 10255 UNI EN 10240 | * | * |  |  |  |  |
| 5.2 | Smooth ends with external PE coating. UNI EN ISO 3183 UNI EN 10220 UNI 9099 | * | * | * | * |  |  |
| 5.3 | Smooth ends, raw UNI ISO EN 3183 UNI EN 10220 | * | * | * | * |  |  |
| 5.4 | External PE-coated smooth ends for A.P. UNI ISO EN 3183 UNI 9099 |  |  |  |  | * | * |

# MATERIALS

Below are the minimum technical requirements required by ITALGAS for each type of pipe.

## Commercial gas pipe (for use at pressures of 0.04  MOP  0.5 bar) welded, with threaded ends, galvanised

Pipe according to UNI EN 10255.

### Metallurgical characteristics of the raw pipe

The metallurgical characteristics must be as follows:

- The steel must be Grade S195T and numerical designation 1.0026;

- The casting analysis of Grade S195T steel must fulfil the requirements set out in Table 1 of UNI EN 10255;

- The Grade S195T steel must have a unit yield strength of ReH min. = 195 MPa, according to UNI EN 10255;

- The mechanical and technological characteristics must comply with the requirements set out in Table 1 of UNI EN 10255.

### Minimum dimensions and masses

Medium-series pipes with dimensions and masses as shown below in Table 2 must be supplied.

Table 2 - Dimensions and masses complying with the requirements in Table 2 of UNI EN 10255

| Material code | DN inches | DN mm | OD mm | T mm | OD max mm | OD min mm | Mass* of the pipe Kg/m |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 32201513105 | 1 | 25 | 33.7 | 3.2 | 34.2 | 33.3 | 2.43 |
| 32201513107 | 1 ½ | 40 | 48.3 | 3.2 | 48.8 | 47.9 | 3.60 |
| 32201513109 | 2 | 50 | 60.3 | 3.6 | 60.8 | 59.7 | 5.10 |
| 32201513112 | 3 | 80 | 88.9 | 4.0 | 89.5 | 88.0 | 8.53 |

*: with threaded and sleeved ends

### Manufacturing process

The manufacturing processes prescribed in point 6 of UNI EN 10255 are permitted.

### Weld bead

Pipes supplied in accordance with this technical specification must be free of any external weld bead. An excess internal weld bead thickness of no more than 0.5 mm + 0.05 t (where t is the nominal pipe thickness in mm) is tolerated.

### Pipe end finish

Unless otherwise specified in the order, the pipe ends must be supplied with tapered threads at both ends in accordance with UNI EN 10226-1 and UNI EN 10226-2 and both protected with a sleeve, screwed, in accordance with UNI EN 10241.

### Pipe length

Unless otherwise stated in the order, the pipe must be supplied in standard lengths of 6 to 6.4 m.

### Pipe marking

This must comply with the requirements set out in point 10 of UNI EN 10255.

### Protective coating

#### Coating

The pipes must be provided with a metal coating consisting of hot dip galvanisation in accordance with UNI EN 10240.

#### Coating marking

This must comply with the requirements set out in point 13 of UNI EN 10240.

### Supply and Testing

#### Production checks and tests

Pipes supplied in accordance with this technical specification must be subjected by the Supplier to all applicable tests prescribed by UNI EN 10255.

#### Inspection documents

The pipes must be delivered with inspection documents in compliance with the standard UNI EN 10204:

- Type 3.1 inspection certificate; or,

- Type 3.2 inspection certificate for ITALGAS inspections.

## PSL 1 Grade L210 pipe (for use at pressures of MOP  12 bar) with smooth ends and PE external coating

PSL 1 pipe conforming to API 5L (UNI EN ISO 3183 where applicable)

### Metallurgical characteristics

The metallurgical characteristics must be as follows:

- Steel must be Grade L210, fulfilling the requirements in Table 1 of API 5L (UNI EN ISO 3183 where applicable);

- The casting analysis of Grade L210 steel must fulfil the requirements of Table 4 of API 5L (UNI EN ISO 3183 where applicable);

- The Grade L210 steel must have a unit yield strength of Rt0.5 min. = 210 N/mm2, fulfilling the requirements of Table 6 of API 5L (UNI EN ISO 3183 where applicable);

- The mechanical and technological characteristics must comply with the requirements in Table 6 of API 5L (UNI EN ISO 3183 where applicable);

### Minimum dimensions and masses of pipes and coating

PSL 1 pipes with dimensions and masses as shown in Table 3 below must be supplied.

Table 3 - Dimensions and masses of steel tubes according to EN 10220

| Material code | DN inches | DN mm | OD mm | T mm | Mass of raw tube Kg/m | Coating thickness mm | Mass of PE coating Kg/m | Mass of PE-coated pipe Kg/m |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 32201526429 | 3/4 | 20 | 26.9 | 2.9 | 1.72 | 1.8 | 0.15 | 1.87 |
| 32201526433 | 1 | 25 | 33.7 | 2.9 | 2.20 | 1.8 | 0.19 | 2.39 |
| 32201526435 | 1 ½ | 40 | 48.3 | 2.9 | 3.25 | 1.8 | 0.26 | 3.51 |
| 32201526437 | 2 | 50 | 60.3 | 2.9 | 4.11 | 1.8 | 0.33 | 4.43 |
| 32201526439 | 2 ½ | 65 | 76.1 | 3.2 | 5.73 | 1.8 | 0.42 | 6.14 |
| 32201526441 | 3 | 80 | 88.9 | 3.2 | 6.76 | 1.8 | 0.48 | 7.24 |
| 32301526443 | 4 | 100 | 114.3 | 3.2 | 8.77 | 1.8 | 0.61 | 9.38 |
| 32201526445 | 5 | 125 | 139.7 | 3.6 | 12.1 | 2.0 | 0.85 | 12.93 |
| 32301526446 | 6 | 150 | 168.3 | 4.0 | 16.20 | 2.0 | 1.00 | 17.20 |
| 32301526447 | 8 | 200 | 219.1 | 5.0 | 26.40 | 2.0 | 1.29 | 27.69 |
| 32301526449 | 10 | 250 | 273.0 | 5.6 | 36.93 | 2.0 | 1.61 | 38.54 |
| 32301526451 | 12 | 300 | 323.9 | 5.6 | 43.96 | 2.2 | 2.10 | 46.05 |
| 32301526453 | 14 | 350 | 355.6 | 6.3 | 54.27 | 2.2 | 2.30 | 56.67 |
| 32301526455 | 16 | 400 | 406.4 | 6.3 | 62.16 | 2.2 | 2.63 | 64.79 |
| 32301526457 | 20 | 500 | 508.0 | 6.3 | 77.95 | 2.2 | 3.28 | 81.23 |
| 32301526460 | 24 | 600 | 610.0 | 7.1 | 105.57 | 2.5 | 4.47 | 110.04 |

### Manufacturing process

- Unless specifically stated in the supply agreements, the pipe manufacturing process must take place:

  - from normalising-rolled strip or thermomechanically rolled strip;

  - by cold forming;

- the welding used to manufacture the pipe must be electric and longitudinal, of the type defined as EW by API 5L (UNI EN ISO 3183 where applicable);

- jointed pipes are not permitted for company use;

- pipes cannot be expanded or cold-expanded.

### Pipe end finish

Pipes must be supplied with smooth ends in accordance with API 5L (UNI EN ISO 3183 where applicable) as prescribed in 9.12.5.1 and 9.12.5.

The ends must therefore be finished as shown in the following figures:

- cut square to the pipe axis for thickness  3.2 mm (Figure 1);

- bevel cut for welding for thicknesses > 3.2 mm (Figure 2).

| Figure 1 | Figure 2 |
| --- | --- |

### Pipe length

- The pipe, unless otherwise stated in the order, must be supplied in running lengths of 8 to 12.5 m.

- The average length of the pipes must be no less than 10 m.

### Pipe marking

This must comply with the requirements of point 11 of API 5L (UNI EN ISO 3183 where applicable).

### External polyethylene coating applied by extrusion

The steel pipe must have an external coating of triple-layer polyethylene in accordance with UNI 9099 with the additions and clarifications contained in the following points.

#### Coating

- The required coating must be as required by UNI 9099 with (R3). It consists of:

- a primer layer, consisting of liquid or powder epoxy resin;

- polyethylene-based adhesive layer;

- external protective layer made of polyethylene;

- Recycled and/or reclaimed polyethylene may not be used;

- The thickness of the polyethylene coating must be class (R);

- The coating adhesion value of 7 N/mm, in accordance with the requirements of UNI 9099, is to be understood as an absolute minimum value.

#### Coating marking

Each pipe must be marked indelibly, in yellow, continuously and on a longitudinal generator. The figures and letters on the coating must be sufficiently large and in any case taller than 4 mm. The marking must highlight:

- The name or acronym of the manufacturer of the uncoated steel tube;

- The name or acronym of the coating manufacturer (if the coating is not applied by the raw pipe manufacturer);

- The reference to the raw pipe standard;

- The reference to UNI 9099;

- The class and designation of the coating;

- The date of application of the coating (month and year);

- The diameter and thickness of the raw pipe.

### Supply and Testing

#### Production checks and tests

- PSL 1 pipes supplied in accordance with this technical specification must be subjected, by the Supplier, to all applicable tests prescribed in point 10 of API 5L (UNI EN ISO 3183 where applicable);

- Italgas reserves the right to be present with its own Italgas Representatives at the tests and examinations envisaged by this technical specification. The Supplier therefore undertakes to give Italgas Representatives free access to the pipe mills, at any time and at any stage of manufacture, and to communicate, reasonably in advance, the date of commencement of pipe manufacture, granting the Representatives full freedom of action, for the necessary inspections, compatibly with production requirements;

- it is understood that the presence of Italgas Representatives during the tests and examinations referred to in the previous point cannot under any circumstance be considered as a replacement for the Supplier's inspections, as the Supplier alone remains responsible for the quality of the pipes produced in its pipe mills;

- the Supplier undertakes to promptly report to Italgas any systematic or random anomaly, affecting either the product or the process, that may occur during the production of Italgas orders.

#### Inspection documents

The pipes must be delivered with inspection documents in compliance with the standard UNI EN 10204:

- Type 3.1 inspection certificate; or,

- Type 3.2 inspection certificate for ITALGAS inspections.

## PSL 1 Grade L210 pipe (for use at pressures of MOP  12 bar) with smooth ends, raw

PSL 1 pipe conforming to API 5L (UNI EN ISO 3183 where applicable)

### Metallurgical characteristics

The metallurgical characteristics must be as follows:

- Steel must be Grade L210, fulfilling the requirements in Table 1 of API 5L (UNI EN ISO 3183 where applicable);

- The casting analysis of Grade L210 steel must fulfil the requirements of Table 4 of API 5L (UNI EN ISO 3183 where applicable);

- The L210 steel must have a unit yield strength of Rt0,5 min. = 210 N/mm2, fulfilling the requirements in Table 6 of API 5L (UNI EN ISO 3183 where applicable);

- The mechanical and technological characteristics must fulfil the requirements in Table 6 of API 5L (UNI EN ISO 3183 where applicable).

### Dimensions and masses minimums of tubes

PSL 1 pipes with dimensions and masses as shown in Table 4 below must be supplied.

Table 4 - Dimensions and masses of steel tubes according to UNI EN 10220

| Material code | DN inches | DN mm | OD mm | T mm | Mass of raw tube Kg/m |
| --- | --- | --- | --- | --- | --- |
| 32201528101 | 3/4 | 20 | 26.9 | 2.9 | 1.72 |
| 32201528102 | 1 | 25 | 33.7 | 2.9 | 2.20 |
| 32201528104 | 1 ½ | 40 | 48.3 | 2.9 | 3.25 |
| 32201528105 | 2 | 50 | 60.3 | 2.9 | 4.11 |
| 32201528107 | 2 ½ | 65 | 76.1 | 3.2 | 5.73 |
| 32301528110 | 3 | 80 | 88.9 | 3.2 | 6.76 |
| 32301528112 | 4 | 100 | 114.3 | 3.2 | 8.77 |
| 32301528114 | 5 | 125 | 139.7 | 3.6 | 12.10 |
| 32301528116 | 6 | 150 | 168.3 | 4.0 | 16.21 |
| 32301528117 | 8 | 200 | 219.1 | 5.0 | 26.40 |
| 32301528119 | 10 | 250 | 273.0 | 5.6 | 36.93 |
| 32301528121 | 12 | 300 | 323.9 | 5.6 | 43.96 |
| 32301528123 | 14 | 350 | 355.6 | 6.3 | 54.27 |
| 32301528125 | 16 | 400 | 406.4 | 6.3 | 62.16 |

### Manufacturing process

- Unless specifically stated in the supply agreements, the pipe manufacturing process must take place:

  - from normalising-rolled strip or thermomechanically rolled strip;

  - by cold forming;

- the welding used to manufacture the pipe must be electric and longitudinal, of the type defined as EW by API 5L (UNI EN ISO 3183 where applicable);

- jointed pipes are not permitted for company use;

- pipes cannot be expanded or cold-expanded.

### Pipe end finish

See point 5.2.4

### Pipe length

See point 5.2.5

### Pipe marking

See point 5.2.6

### Supply and Testing

See point 5.2.8

## PSL 2 Grade L360N pipe (for use at pressures of 12  MOP  75 bar) with smooth ends and PE external coating

PSL 2 pipe conforming to API 5L (UNI EN ISO 3183 where applicable)

### Metallurgical characteristics

The metallurgical characteristics must be as follows:

- Steel must be Grade L360N, fulfilling the requirements in Table 1 of API 5L (UNI EN ISO 3183 where applicable);

- The casting analysis of L360N steel must fulfil the requirements in Table 5 of API 5L (UNI EN ISO 3183 where applicable);

- The L360N steel must have a unit yield strength Rt0,5 min. = 360 N/mm2, fulfilling the requirements in Table 7 of API 5L (UNI EN ISO 3183 where applicable);

- The mechanical and technological characteristics must fulfil the requirements in Table 7 of API 5L (UNI EN ISO 3183 where applicable).

### Minimum dimensions and masses of pipes and coating

Steel pipes must comply with API 5L (UNI EN ISO 3183 where applicable) and have dimensions and masses as shown below in Table 5.

Table 5 - Dimensions and masses

| Material code |  | DN inches |  | DN mm |  | OD mm |  | T mm |  | Mass of raw tube Kg/m |  | Coating thickness mm |  | Mass of PE coating Kg/m |  | Mass of PE-coated pipe Kg/m |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 32301529914 |  | 3 |  | 80 |  | 88.9 |  | 4.0 |  | 8.38 |  | 1.8 |  | 0.48 |  | 8.86 |
| 32301529918 |  |  |  |  |  |  | 5.5 |  | 11.30 |  | 1.8 |  | 0.48 |  | 11.78 |  |
| 32301529928 |  | 4 |  | 100 |  | 114.3 |  | 4.0 |  | 10.90 |  | 1.8 |  | 0.61 |  | 11.51 |
| 32301529930 |  |  |  |  |  |  | 5.6 |  | 15.00 |  | 1.8 |  | 0.61 |  | 15.61 |  |
| 32301529934 | 5 |  | 125 |  | 139.7 |  | 6.3 |  | 20.70 |  | 2.0 |  | 0.85 |  | 21.55 |  |
| 32301529935 |  |  |  |  |  |  | 7.1 |  | 23.20 |  | 2.0 |  | 0.85 |  | 24.05 |  |
| 32301529946 |  | 6 |  | 150 |  | 168.3 |  | 7.1 |  | 28.20 |  | 2.0 |  | 1.00 |  | 29.20 |
| 32301529948 |  |  |  |  |  |  | 8.0 |  | 31.60 |  | 2.0 |  | 1.00 |  | 32.60 |  |
| 32301529955 |  | 8 |  | 200 |  | 219.1 |  | 7.0 |  | 36.60 |  | 2.0 |  | 1.29 |  | 37.89 |
| 32301529958 |  |  |  |  |  |  | 10.0 |  | 51.60 |  | 2.0 |  | 1.29 |  | 52.89 |  |
| 32301529961 |  | 10 |  | 250 |  | 273.0 |  | 7.8 |  | 51.03 |  | 2.0 |  | 1.61 |  | 52.64 |
| 32301529963 |  |  |  |  |  |  | 11.1 |  | 71.71 |  | 2.0 |  | 1.61 |  | 73.32 |  |
| 32301529974 |  | 12 |  | 300 |  | 323.9 |  | 7.1 |  | 55.50 |  | 2.2 |  | 2.10 |  | 57.60 |
| 32301529975 |  |  |  |  |  |  | 9.5 |  | 73.65 |  | 2.2 |  | 2.10 |  | 75.75 |  |
| 32301529980 |  | 14 |  | 350 |  | 355.6 |  | 7.9 |  | 67.76 |  | 2.2 |  | 2.30 |  | 70.06 |
| 32301529981 |  |  |  |  |  |  | 10.3 |  | 87.69 |  | 2.2 |  | 2.30 |  | 89.99 |  |
| 32301529992 |  | 16 |  | 400 |  | 406.4 |  | 8.7 |  | 85.34 |  | 2.2 |  | 2.63 |  | 87.97 |
| 32301529993 |  |  |  |  |  |  | 11.1 |  | 107.93 |  | 2.2 |  | 2.63 |  | 110.56 |  |
| 32301529995 |  | 20 |  | 500 |  | 508.0 |  | 11.1 |  | 136.20 |  | 2.2 |  | 3.28 |  | 139.48 |
| 32301529997 |  | 24 |  | 600 |  | 610.0 |  | 11.1 |  | 163.47 |  | 2.5 |  | 4.47 |  | 167.94 |

#### PSL 2 Grade L245N pipe (for use at pressures of 12  MOP ≤ 24 bar) - Metallurgical characteristics

Limited for use at pressures 12 < MOP ≤ 24 bar, as an alternative to PSL 2 Grade L360N steel pipe, PSL 2 Grade L245N steel pipe is permissible for company use.

The metallurgical characteristics must be as follows:

- Steel must be Grade L245N, fulfilling the requirements in Table 1 of API 5L (UNI EN ISO 3183 where applicable);

- The casting analysis of L245N steel must fulfil the requirements in Table 5 of API 5L (UNI EN ISO 3183 where applicable);

- The L245N steel must have a unit yield strength of Rt0,5 min. = 245 N/mm2, fulfilling the requirements in Table 7 of API 5L (UNI EN ISO 3183 where applicable);

- The mechanical and technological characteristics must comply with the requirements in Table 7 of API 5L (UNI EN ISO 3183 where applicable);

#### PSL 2 Grade L245N pipe (for use at pressures of 12  MOP  24 bar) - Minimum dimensions and masses of pipe and coating

Steel pipes must comply with API 5L (UNI EN ISO 3183 where applicable) and have dimensions and masses as shown below in Table 6.

Table 6 - Dimensions and masses

| Material code | DN inches | DN mm | OD mm | T mm | Mass of raw tube Kg/m | Coating thickness mm | Mass of PE coating Kg/m | Mass of PE-coated pipe Kg/m |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 32301529514 | 3 | 80 | 88.9 | 3.2 | 6.76 | 1.8 | 0.48 | 7.24 |
| 32301529528 | 4 | 100 | 114.3 | 3.2 | 8.77 | 1.8 | 0.61 | 9.38 |
| 32301529534 | 5 | 125 | 139.7 | 3.6 | 12.10 | 2.0 | 0.85 | 12.95 |
| 32301529545 | 6 | 150 | 168.3 | 4.0 | 16.20 | 2.0 | 1.00 | 17.20 |
| 32301529555 | 8 | 200 | 219.1 | 4.5 | 23.80 | 2.0 | 1.29 | 25.09 |
| 32301529561 | 10 | 250 | 273.0 | 5.0 | 33.00 | 2.0 | 1.61 | 34.61 |
| 32301529574 | 12 | 300 | 323.9 | 6.3 | 49.30 | 2.2 | 2.10 | 51.40 |
| 32301529580 | 14 | 350 | 355.6 | 6.3 | 54.30 | 2.2 | 2.30 | 56.60 |
| 32301529592 | 16 | 400 | 406.4 | 8.0 | 78.60 | 2.2 | 2.63 | 81.23 |
| 32301529595 | 20 | 500 | 508.0 | 10.0 | 123.00 | 2.2 | 3.28 | 126.28 |

### Manufacturing process

- Unless specifically stated in the supply agreements, in accordance with Table 3 of API 5L (UNI EN ISO 3183 where applicable), the pipe manufacturing process must take place:

  - from normalising-rolled strip;

  - by cold forming;

- the welding used to manufacture the pipe must be electric and longitudinal, of the type defined as HFW by API 5L (UNI EN ISO 3183 where applicable);

- Jointed pipes are not permitted for company use;

- Welding of strip ends is not permitted in the pipe;

- Tubes may not be expanded or cold-expanded.

### Pipe end finish

See point 5.2.4

### Pipe length

See point 5.2.5

### Pipe marking

See point 5.2.6

### External polyethylene coating applied by extrusion

See point 5.2.7

### Supply and Testing

#### Production checks and tests

- PSL 2 pipes supplied in accordance with this technical specification must be subjected, by the Supplier, to all applicable tests prescribed in point 10 of API 5L (UNI EN ISO 3183 where applicable);

- Italgas reserves the right to be present with its own Italgas Representatives at the tests and examinations envisaged by this technical specification. The Supplier therefore undertakes to give Italgas Representatives free access to the pipe mills, at any time and at any stage of manufacture, and to communicate, reasonably in advance, the date of commencement of pipe manufacture, granting the Representatives full freedom of action, for the necessary inspections, compatibly with production requirements;

- it is understood that the presence of Italgas Representatives during the tests and examinations referred to in the previous point cannot under any circumstance be considered as a replacement for the Supplier's inspections, as the Supplier alone remains responsible for the quality of the pipes produced in its pipe mills;

- the Supplier undertakes to promptly report to Italgas any systematic or random anomaly, affecting either the product or the process, that may occur during the production of Italgas orders.

#### Inspection documents

The pipes must be delivered with inspection documents in compliance with the standard UNI EN 10204:

- Type 3.1 inspection certificate; or,

- Type 3.2 inspection certificate for ITALGAS inspections.

# DOCUMENTATION FOR “THE APPROVAL FOR COMPANY USE PROCESS”

The prospective supplier must submit the following documentation at the tender stage:

to the PROMA-CMMAT Department:

- “Declaration of conformity” with this technical specification and any specific documents mentioned in it (legal provisions, applied standards, MID Directive, ATEX, EMC, PED, etc.) to which the supplier refers for the design and construction of the product, as indicated in the UNI CEI EN ISO/IEC 17050-1 standard (see the example given in APPENDIX 1 of this technical specification);

# TESTS AND INSPECTIONS

- See relevant items 5.1.9 - 5.2.8 - 5.3.7 - 5.4.11 of Supply and Testing.

- In order to verify the conformity of the proposed products with the contents of this technical specification and the cited standards to which reference is made, it is Italgas' right, for each purchase order, to request from the Supplier:

- To produce further technical documentation and/or drawings;

- The performance of any laboratory and/or field tests.

# REFERENCE STANDARDS

- Decree of 16.04.2008 on “Technical regulations for the design, construction, testing, operation and supervision of works and plants for the transmission of natural gas with a density not exceeding 0.8”.

- Decree of 17 April 2008 on “Technical regulations for the design, construction, testing, operation and supervision of works and plants for the transmission of natural gas with a density not exceeding 0.8”.

- UNI 9099 - “External polyethylene coating applied by extrusion. Steel pipes used for buried or submerged pipelines"

- UNI CEI EN ISO/IEC 17050-1 - “Conformity assessment. Supplier's declaration of conformity. Part 1: General requirements”

- UNI EN 10079 - “Definition of steel products”

- UNI EN 10204 - “Metallic products. Types of inspection documents”

- UNI EN 10226-1 - "Pipe threads for thread seal coupling - Part 1: Tapered External and Parallel Internal Threads - Dimensions, Tolerances and Designation"

- UNI EN 10226-2 - "Pipe threads for thread seal coupling - Part 2: Tapered External and Parallel Internal Threads - Dimensions, Tolerances and Designation"

- UNI EN 10240 - "Internal and/or external protective coatings for steel tubes. Specification for hot dip galvanized coatings applied in automatic plants'

- UNI EN 10241 - "Steel threaded pipe fittings."

- UNI EN 10255 - "Non-alloy steel tubes suitable for welding and threading. Technical Terms of Delivery"

- UNI EN ISO 3183 - “Petroleum and natural gas industries - Steel pipe for pipeline transportation systems”

- UNI 9034 - “Gas distribution pipelines with maximum operating pressure (MOP) not exceeding 0.5 MPa (5 bar) - Materials and jointing systems"

- UNI 10220 - "Seamless and welded steel tubes - Dimensions and masses per unit length"

- API 5L

# APPENDICES

Appendix 1 - “Sample declaration of conformity”

Appendix 1

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN ISO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(4)	S.T.V.F.C.  15AA300	WELDED STEEL PIPES FOR METHANE GAS PIPELINES	Edition 2 of 30/09/2022

Additional information:

(5) 	...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(6) 	............................................................. 			......................................................................................................................

(Name and position) 						(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- List all the products for which approval for company use is requested (name, type, model), stating any codes assigned by the Supplier itself and, where existing, the relevant material codes assigned by Italgas Reti.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

Supplier means the entity responsible for the design and construction of the products or its legal representative as defined in Legislative Decree no. 206 of 6 September 2005 - "CONSUMER CODE pursuant to Article 7 of Law no. 229 of 29 July 2003".