- “TECHNICAL SPECIFICATION FOR EVALUATION, SUPPLY AND TESTING”

- S.T.V.F.C. 1627300

- Polyethylene pipes for methane gas pipelines

| Compiled by | APT-ATECH-NORM | MARELLA MANUELE |
| --- | --- | --- |
|  | APT-ATECH-NORM | NORDIO IVANO |
| Checked by | APT-ATECH-NORM | CIMINO SALVATORE |
| Checked by | PROMA-MATMA | SCOTTO ENRICO |
| Checked by | BDT | AMBROSI LEONARDO |
| Checked by | PROMA/CMMAT | FASSINO SILVIO |
| Checked by | HSEQ | LIMONTA AGOSTINO MASSIMO |
| Approved by | APT-ATECH | GHIBAUDO CLAUDIO |

SUMMARY

1	PRELIMINARY INFORMATION	3

1.1	Cancels and replaces	3

1.2	Reason for issue	3

1.3	Company departments mentioned in the document	3

1.4	Definitions	3

2	PURPOSE AND FIELD OF APPLICATION	3

2.1	Purpose	3

2.2	Field of application	3

3	SPECIFICATIONS	3

4	TECHNICAL CHARACTERISTICS	4

4.1	Raw material	4

4.2	Pipes	4

4.3	Technical assessment	5

5	Marking	6

6	TYPE TEST	6

7	DOCUMENTATION REQUIRED FROM THE SUPPLIER	6

7.1	Supplier	7

7.2	Documentation for the company approval process	7

7.3	Test Documentation	7

7.4	Supply Documentation	7

8	TESTS AND INSPECTIONS	7

8.1	Tensile strength test for butt welding	8

8.2	Right of the client	8

9	CONDITIONS OF SUPPLY	8

9.1	Packaging	10

9.2	Shipping	11

10	REFERENCE STANDARDS	11

11	APPENDICES	11

Appendix 1	12

# PRELIMINARY INFORMATION

## Cancels and replaces

This specification cancels and replaces the S.T.V.F.C. 1627300, edition 4, dated 21 November 2018 – "Polyethylene pipes for natural gas pipelines".

## Reason for issue

Updating of S.T.V.F.C. 1627300 was necessary due to:

- national regulatory update;

- the introduction of new diameters OD 75-110-140-160-200-250-280 SDR (Standard Dimension Ratio) 11 (S5) and OD 110-140-160-200-250-280 SDR (Standard Dimension Ratio) 17 (S8).

## Company departments mentioned in the document

- PROMA-CMMAT- Category Manager Materials

## Definitions

The technical definitions contained in this specification conform to those of the standards listed in Section 10 “Reference standards”.

# PURPOSE AND FIELD OF APPLICATION

## Purpose

This Specification defines the technical characteristics, the accompanying documentation, the criteria for supply and testing, and the procedures for carrying out the technical inspections to be performed for the approval for company use of polyethylene pipes for methane.

## Field of application

It applies whenever material covered by this specification must be authorised for company use, produced

by a new potential Supplier or by an existing one.

# SPECIFICATIONS

- These specifications must be understood as an integral part of the "ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS."

- this specification contains the minimum technical requirements demanded by Italgas Reti based on the reference Legislative and Technical Standards;

- it is the Supplier's responsibility to ensure that the products supplied fully comply with the provisions of this technical specification and the applicable standards;

- if the products in question are supplied by an installer, the installer must document their compliance as required under “Documentation required from the Supplier”;

- it is the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. sharp edges or incorrect directions for use and maintenance), which may jeopardise the health and safety of the Client's workers in relation to the provisions of Legislative Decree no. 81/08, as amended and supplemented;

- the drawings or illustrations shown should be considered as a "standard model shown as an example", except for the specified dimensions and technical characteristics, which should be considered as binding;

- for all technical and operational aspects that conflict with or are not mentioned in this technical specification but that nevertheless pertain to the design, installation, maintenance and use of the products themselves, it is the Supplier's responsibility to refer to the regulations in force;

- Italgas Reti reserves the right, in the overall assessment of the products proposed, to also consider the operational maintenance instructions for the devices as described in the relative instructions.

# TECHNICAL CHARACTERISTICS

Below are the technical characteristics that the products covered by this technical specification must meet.

## Raw material

This must comply with the requirements of UNI EN 1555-1 with the following additions:

- only virgin raw material must be used: the use of previously extruded polyethylene, even if regenerated, recycled and/or from the same production, is not permitted;

- pigmented material in the colours indicated in Table 3 must be used for the stripes;

- must be certified by the compound manufacturer in accordance with UNI EN 10204 “type 3.1” as being at least PE 80 bimodal or PE 100;

- raw material composition certificates must be provided for each "batch" of pipes.

## Pipes

The pipes must be certified in accordance with the requirements of UNI EN 10204 "type 3.1".

The length of the pipes, unless otherwise stated in the order, must be:

- in 6 m bars up to and including OD 63;

- in 12 m bars over OD 63;

- in rolls of 50 m or 100 m (according to order) up to OD 90 and only for SDR 11 (S5)

The pipes normally used by Italgas Reti are shown in Tables 2 and 3.

Table 1 Series of diameters and thicknesses for SDR 17 (S8) pipes

| - Code - Material | - Outer diameter - OD (mm) | - Thickness - SDR 17 (S8) - mm |  |
| --- | --- | --- | --- |
| - 27601637127 | - 90 | - 5.4 |  |
| - 27601637129 | - 110 | - 6.6 |  |
| - 27601637133 | - 125 | - 7.4 |  |
| - 27601637135 | - 140 | - 8.3 |  |
| - 27601637137 | - 160 | - 9.5 |  |
| - 27601637142 | - 180 | - 10.7 |  |
| - 27601637145 | - 200 | - 11.9 |  |
| - 27601637148 | - 225 | - 13.4 |  |
| - 27601637151 | - 250 | - 14.8 |  |
| - 27601637153 | - 280 | - 16.6 |  |
| - 27601637150 | - 315 | - 18.7 |  |

Table 2 Series of diameters and thicknesses for SDR 11 (S5) pipes

| - Code - Material | - Outer diameter - OD (mm) | - Thickness - SDR 11 (S5) - mm |
| --- | --- | --- |
| 27601627106 | - 20 | - 3.0 |
| 27601627112 | - 32 | - 3.0 |
| 27601627118 | - 50 | - 4.6 |
| 27601627121 | - 63 | - 5.8 |
| 27601627125 | - 75 | - 6.8 |
| 27601627127 | - 90 | - 8.2 |
| 27601627129 | - 110 | - 10.0 |
| 27601627133 | - 125 | - 11.4 |
| 27601627135 | - 140 | - 12.7 |
| 27601627137 | - 160 | - 14.6 |
| 27601627142 | - 180 | - 16.4 |
| 27601627145 | - 200 | - 18.2 |
| 27601627148 | - 225 | - 20.5 |
| 27601627151 | - 250 | - 22.7 |
| 27601627153 | - 280 | - 25.4 |
| 27601627150 | - 315 | - 28.6 |

- The material characteristics and reference standards for production, inspection and certification must meet the following standards:

- UNI EN 1555 parts 1 and 2;

- UNI CEN/TS 1555 part 7;

- UNI 9034.

## Technical assessment

- In relation to Legislative Decree no. 81/08, as amended and supplemented, Italgas Reti reserves the right, in its evaluation of the use of the proposed products, to consider the operational consequences deriving from the conditions of use of the equipment as prescribed by the Supplier in the "Use and Maintenance Manual".

# Marking

- The marking of pipes must be in accordance with UNI EN 1555 Part 2 "Pipes".

Pipes must be coloured in accordance with UNI EN 1555 Part 2, and in accordance with Table 3 below:

Table 3 - Colours and Marking

| PE 80 | PE 100 | MARKING |
| --- | --- | --- |
| BLACK YELLOW | BLACK ORANGE | The marking must be in a colour that clearly contrasts with the colour of the pipe. The co-extruded stripes on the black pipes must be yellow for PE 80 and orange for PE 100 and be of the same raw material as the pipe. |

# TYPE TEST

The tests must be carried out in accordance with the requirements of UNI EN 1555-7, section 6.2.

# DOCUMENTATION REQUIRED FROM THE SUPPLIER

## Supplier

The potential Supplier must be qualified as an Italgas Supplier.

## Documentation for the company approval process

The potential Supplier must submit the following documentation to the PROMA/CMMAT Department at the tender stage:

- “Declaration of Conformity” with this technical specification and any specific documents (legislative provisions, applied standards, etc.) to which the Supplier refers for the design and construction of the product, in accordance with the requirements of UNI CEI EN ISO/IEC 17050-1 (see the example in APPENDIX 1 to this technical specification).

## Test Documentation

The Supplier must issue a “type 3.1” Inspection Certificate in accordance with UNI EN 10204, which states that the products provided are compliant with the requirements of these specifications and which provides the test results.

Registration of the full production/test documentation completed by the Supplier must be kept (on the basis of legal provisions) for 10 years under its responsibility, and must be made available whenever requested by the Client.

## Supply Documentation

- Documents compliant with Legislative Decree no. 286 of 21 November 2005, as amended;

- Inspection and quality plan and testing procedures;

- “Type 3.1” Inspection and Material Certificates in accordance with UNI EN 10204;

- Approved technical product documentation.

- Preliminary technical documentation describing the product, including information on the material, construction drawings, dimensional characteristics, tests and inspections required by the Supplier's standard, etc;

- Statement certifying ownership to market the product;

- Whatever else the potential Supplier considers useful to better qualify the proposed product.

# TESTS AND INSPECTIONS

Italgas Reti reserves the right:

- To be present with its own Inspectors and/or Inspection Companies appointed by the same to carry out tests/checks c/o the Supplier's plant and at the Supplier's care and expense, to check the constructive and functional compliance of the materials in accordance with the specifications and/or reference standards.

- To verify, upon receipt and/or under actual conditions of use, the perfect compliance of the goods with the functional technical characteristics expressly indicated in the Contract.

It remains understood that the favourable outcome of the Inspection and checking of the materials shall not release the Supplier in any way from its responsibilities and obligations arising from every individual Contract.

The tests, trials and inspections shall be carried out in accordance with this specification and the following Standards:

- UNI EN ISO 1555-1

- UNI EN ISO 1555-2

- UNI EN ISO 1555-5

The results and the manner in which the tests were carried out must be recorded in the “type 3.1” Inspection Certificate in accordance with UNI EN 10204.

## Tensile strength test for butt welding

- The performance of this test, carried out in compliance with the ISO 13953 standard and according to the evaluation criterion of the UNI EN 1555-7 standard, must be guaranteed and certified by the Supplier in accordance with UNI EN 10204 point 3.1 for each pipe batch/lot intended for Italgas.

## Right of the client

It is Italgas Reti's right, for each purchase order, to request from the Supplier:

- further technical/graphic documentation;

- additional laboratory and/or field tests;

- performance of factory Tests/Trials/Checks

In order to verify the conformity of the proposed products with this technical specification and the cited standards to which reference is made.

# CONDITIONS OF SUPPLY

In accordance with the Supplier's Standard in compliance with Legislative Decree no. 152 of 3 April 2006 as amended and supplemented.

In particular, upon delivery to the Client, the pipes must not present any form of deterioration and must be laid on supports that ensure that they do not come into contact with each other and allow easier unloading using cranes, overhead travelling cranes or forklift trucks.

On the means of transport, the pipes must be stowed on interposed supports in such a way that they do not cause abrasion or damage to the pipes themselves and their surface, and their arrangement must be such that they cannot roll in any way (use of wedges or other type of blocking) and thus compromise the stability of the stack or of the individual pipes being transported.

The pipes must not be dragged over any surface in any way, nor must they collide with each other. Pipes must be handled without causing deterioration.

When handling pipes, the use of any equipment of a shape or nature that could damage the surface is forbidden.

The Supplier must carry out an appropriate control and inspection process to ensure that the supply and transport comply with the requirements of applicable legislation, supplied specifications and all safety-related legislative aspects.

The marking of the pipes must be stamped on all supplied diameters and contain the information according to EN 1555 part 2 "Pipes".

## Packaging

Packaging must be optimised to minimise waste on the construction site. The materials used for packaging and transport must not in any case be harmful to the environment and the health of workers and must guarantee adequate stability and safety during unloading in compliance with the regulations in force.

The ends of the pipes must be smooth and fitted with suitable plastic protective caps with a small hole to allow air to escape as a result of expansion.

All pipes must be placed on the transport vehicle in packages that can be handled either by crane or forklift truck.

Pipes with an OD < 90, supplied in bars, must be tied together in bundles with flexible plastic straps at least 30 mm wide and no more than 2 m apart.

Pipes with an OD ≥ 90 must be packed in framed blocks, consisting of at least four frames of rigid wooden laths, at least 100 mm wide and firmly joined together; perfect block clamping must then be ensured by flexible plastic straps as described above, placed in all intermediate spaces between the laths.

Pipes supplied in coils must also be firmly bound by means of the flexible plastic straps described above, positioned in such a way as to allow uncoiling to be carried out as smoothly as possible and in compliance with the safety conditions defined by Legislative Decree o. 81/08 as amended and supplemented. (see the illustrative example in Figure 1). For special requirements, it may be requested that the rolls are delivered, and kept until use, on special reels or on special trolleys.

Main strapping

Intermediate strapping

Figure 1

## Shipping

Pipes must be supplied no more than 9 (nine) months after production.

The Supplier must cover all charges resulting from any deliveries of pipes to Italgas Reti that do not comply with the requirements.

# REFERENCE STANDARDS

- UNI CEI EN ISO/IEC 17050 - 1 - "Conformity assessment - Supplier's declaration of conformity - Part 1: General requirements".

- Ministerial Decree of 16 April 2008 on “Technical regulations for the design, construction, testing, operation and supervision of works and plants for the transmission of natural gas with a density not exceeding 0.8”.

- Ministerial Decree of 17 April 2008 on “Technical regulations for the design, construction, testing, operation and supervision of works and plants for the transmission of natural gas with a density not exceeding 0.8”.

- Legislative Decree No. 286 of 21 November 2005: as subsequently amended and supplemented. - “Provisions for the regulatory reorganisation of the regulated liberalisation of the road haulage business”.

- Legislative Decree No. 152 of 03 April 2006 as subsequently amended and supplemented. - “Environmental standards”.

- Legislative Decree No. 81 of 09 April 2008 as subsequently amended and supplemented. - “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”.

- UNI EN 1555 - “Plastic piping systems for the supply of gaseous fuels - Polyethylene (PE):

- “Part 1 – General.”

- “Part 2 – Pipes.”

- “Part 5 – Fitness for purpose of the system”.

- “Part 7 – Guidance for the assessment of conformity”.

- UNI 9034 - “Gas distribution pipelines with maximum operating pressure (MOP) not exceeding 0.5 MPa (5 bar) - Materials and jointing systems”.

- UNI EN 10204 - “Metallic products - Types of inspection documents”.

- ISO 13953 - "Polyethylene (PE) pipes and fittings - Determination of the tensile strength and failure mode of test pieces from a butt-fused joint".

# APPENDICES

- APPENDIX 1 – “Sample declaration of conformity with this technical specification”

### Appendix 1

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN ISO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

(4)	The following products manufactured by us:

| Our material code (5) | Italgas Reti material code (6) |
| --- | --- |
| xxx | 1627027 |
| xxx | xxx |

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(7)	S.T.V.F.C. 1627300	POLYETHYLENE PIPES FOR METHANE GAS PIPELINES	Edition 5 of 30/09/2022

Additional information:

(8) 	...............................................................................................................................................................................................

...............................................................................................................................................................................................

...............................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(9) 	.............................................................		...................................................................................................................

(Name and position)				(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- The “subject” must be unambiguously described so that the declaration of conformity can be referred to the subject in question.

- List all the products for which company use authorisation is being requested.

- For each individual product supplied, state the material code used by the Supplier.

- For each individual product supplied, please quote the material code assigned by Italgas Reti, which can be found in the Italgas Reti reference documents.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

Supplier means the party responsible for the design and construction of the products or its legal representative as defined in Legislative Decree no. 206 of 6 September 2005 as amended and supplemented. - "CONSUMER CODE" pursuant to Article 7 of Law no. 229 of 29 July 2003.