“TECHNICAL SPECIFICATION FOR EVALUATION, SUPPLY AND TESTING”

S.T.V.F.C. 2000300

Steel valves for gas pipelines

| Compiled by | SERTEC-NORM | GIARAMIDA |
| --- | --- | --- |
| Checked by | SERTEC-NORM | VARESE |
| Checked by | HSEQ | BOLZONI |
| Checked by | PROMA-MATMA | SCOTTO |
| Checked by | SERTEC-LAB | SALATI |
| Checked by | PROMA/CMMAT | FASSINO |
| Approved by | SERTEC | COMAZZI |

SUMMARY

1	PRELIMINARY INFORMATION	4

1.1	Cancels and replaces	4

1.2	Reason for issue	4

1.3	Company departments mentioned in the document	4

1.4	Definitions	4

2	PURPOSE AND FIELD OF APPLICATION	4

2.1	Purpose	4

2.2	Field of application	4

3	SPECIFICATIONS	5

4	OPERATING CONDITIONS	5

4.1	Operating temperature	5

4.2	Flow velocity	5

4.3	Pressure range	5

5	GENERAL REGULATORY REQUIREMENTS	6

5.1	Construction, maintenance, use	6

5.2	Use in potentially explosive atmospheres	6

5.3	Pressure equipment	6

5.4	Operation of valves	7

5.5	Checking the closing/opening of valves in service	7

6	TECHNICAL CHARACTERISTICS	7

6.1	Plug valves	7

6.1.1	OP ≤ 0.5 MPa (5 bar)	7

6.1.2	OP > 0.5 MPa (5 bar)	7

6.2	Ball valves	8

6.2.1	OP ≤ 0.5 MPa (5 bar)	8

6.2.2	0.5 MPa (5 bar) ≤ OP ≤ 1.6 MPa (16 bar)	8

6.2.3	OP ≥ 1.6 MPa (16 bar)	8

6.3	Butterfly valves	9

6.4	Body material	9

6.5	Butt-weld body ends	9

6.5.1	Tapering of valve body end	9

6.6	Characteristics of pipes used by Italgas Reti	10

6.6.1	Pipes used by ITALGAS RETI for MOP ≤ 1.2 MPa (12 bar)	10

6.6.2	Pipes used by ITALGAS RETI for MOP  1.2 MPa (12 bar) and ≤ 7.5 MPa (75 bar)	11

6.7	Operating device	12

6.7.1	Fixed operating element	12

6.7.2	Removable operating element	12

6.7.3	Operating device extensions	12

6.8	Position indicator (Obturator position)	13

6.9	Protective coating	13

6.9.1	Ball/Plug valves for underground use	13

6.9.2	Ball valves for atmospheric or manhole use	13

6.9.3	Butterfly valves	13

6.10	Technical assessment	13

7	MARKING	14

8	TYPE TEST	14

9	TEST CONDITIONS	15

9.1	Right of the Client	15

9.2	Tests and inspections	15

10	CONDITIONS OF SUPPLY	15

11	DOCUMENTATION REQUIRED FROM THE SUPPLIER	16

11.1	Supplier	16

11.2	Documents to be submitted	16

11.3	Test Documentation	16

11.4	Supply Documentation	16

11.5	Right of the Client	17

12	REFERENCE STANDARDS	17

13	APPENDICES	19

Appendix 1	20

Appendix 2	21

Appendix 3	22

Appendix 3	23

Appendix 4	24

Appendix 4	25

Appendix 5	26

Appendix 6	27

Appendix 7	28

Appendix 8	29

Appendix 9	30

Appendix 10	31

Appendix 11	32

Appendix 12	33

Appendix 13	34

Appendix 14	35

Appendix 15	36

# PRELIMINARY INFORMATION

## Cancels and replaces

This specification cancels and replaces:

- S.T.V. 2000300, version 3, dated 26.05.2009 - 'Steel valves for gas pipelines';

- Technical Specification 2000300, rev. 1, dated 02.09.1993 - 'Steel Valves'.

## Reason for issue

Updating the S.T.V. 2000300 and its reissue in the form of Technical Specifications for Assessment and Supply and Testing (S.T.V.F.C.), became necessary as a result of:

- New legislative context;

- Issuing of new national and European standards (e.g. UNI, CEI, EN, etc.)

- Inclusion of Supply and Testing Criteria.

## Company departments mentioned in the document

- SERTEC-NORM = Standard

- PROMA-CMMAT = Category Manager Materials

## Definitions

The technical definitions contained in this specification conform to those of the standards listed in point 13  “Reference standards”.

# PURPOSE AND FIELD OF APPLICATION

## Purpose

This specification defines the technical characteristics, the accompanying documentation, the criteria for supply and testing, and the manner in which technical inspections are to be carried out for the production of steel valves for gas pipelines (natural gas), taking into account that any additives present in the gas are non-corrosive.

## Field of application

This Technical Specification applies whenever the steel valves referred to herein, produced by a new potential Supplier or by an existing Supplier, may need to be supplied.

# SPECIFICATIONS

- These specifications must be understood as an integral part of the "ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS."

- This specification contains the minimum technical requirements demanded by Italgas Reti based on the reference Legislative and Technical Standards.

- It is the Supplier's responsibility to ensure that the products supplied fully comply with the provisions of this technical specification and the applicable standards.

- if the products in question are supplied by an installer, the installer must document their compliance as required under “Documentation required from the Supplier”.

- It is the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. sharp edges, incorrect directions for use and maintenance, etc.), which may jeopardise the health and safety of the Client's workers in relation to the provisions of Legislative Decree no. 81/08, as amended and supplemented.

- For any technical and operational aspects that conflict with or are not mentioned in this technical specification but that nevertheless pertain to the design, installation, maintenance and use of the products themselves, it is the Supplier's responsibility to refer to the regulations in force.

- The drawings or illustrations shown should be considered as a "standard model shown as an example", except for the specified dimensions and technical characteristics, which should be considered as binding.

# OPERATING CONDITIONS

## Operating temperature

The design temperature must be between -10°C and +60°C

## Flow velocity

The flow velocity is according to the Ministerial Decrees.

## Pressure range

The maximum operating pressures are given in Appendices 1 to 14.

# GENERAL REGULATORY REQUIREMENTS

All the valves described in this specification must be:

- Manufactured, controlled and certified in accordance with the legal and technical standards stated in the following points and in the various Appendices;

- Accompanied by "Operating Instructions" in Italian as required by the reference standards.

## Construction, maintenance, use

All valves, in relation to the operating pressure range used, must comply with the requirements of the following Ministerial Decrees and the Technical Standards referred to therein:

- Ministerial Decree of 16 April 2008;

- Ministerial Decree of 17 April 2008.

## Use in potentially explosive atmospheres

All valves must be able to be used without risk within potentially explosive atmospheres and therefore, with reference to Legislative Decree 233 of 12 June 2003, must comply with the provisions of Legislative Decree no. 85 of 19 May 2016 where applicable.

Compliance with this requirement must be demonstrated, if the product falls within the scope of Legislative Decree No. 85 of 19 May 2016, by :

- Product "marking";

- Documentation required, as appropriate, by the aforementioned Decree and by the relevant harmonised standards (e.g. EU declaration of conformity or certificate of conformity, operating and maintenance instructions in Italian, any certificate of conformity following EU type-examination).

Appendices 1 to 14 list the hazardous locations with the relevant areas where the valves are to be installed and for which the manufacturer must carry out a risk analysis at its own responsibility.

## Pressure equipment

The valves described in this specification are used in the construction and operation of pressure networks conveying natural gas or pressure reduction systems. They must therefore also comply with the provisions of Legislative Decree no. 93 of 25 February 2000, as amended. (PED Directive).

In accordance with the PED Directive, the following harmonised standards in particular must be applied as far as relevant:

- UNI EN 19 - "Industrial valves - Marking of metal valves"

- UNI EN 1983 - “Steel ball valves”

- UNI EN 593 - “Metal butterfly valves”

- UNI EN 1092-1 - "Flanges and their joints - Part 1: Steel flanges”

## Operation of valves

In compliance with the legal provisions in force on the use and operation of equipment (Ref. Legislative Decree no. 81 of 9 April 2008 as amended), it is the Supplier's responsibility to equip the valves that require it, with fittings (e.g. eyebolts) to enable them to be operated by lifting means.

## Checking the closing/opening of valves in service

Once a year, Italgas Reti checks the closing/opening of the valves installed in its networks. The valves supplied to Italgas Reti must therefore maintain their efficiency characteristics for the period between one operation of the same and the next.

# TECHNICAL CHARACTERISTICS

## Plug valves

### OP ≤ 0.5 MPa (5 bar)

Reference legislation:

- Ministerial Decree of 16 April 2008

Technical standards referred to in the Ministerial Decree:

- Standard UNI 9034

- Standard API SPEC 6D

or:

- Standard UNI EN 12007-1

- Standard UNI EN 12007-3

- Standard UNI EN 13774 and complementary standards referred to therein

The valve types with related ND and construction requirements are indicated in Appendix 1

### OP > 0.5 MPa (5 bar)

Reference legislation:

- Ministerial Decree of 17 April 2008

Technical standards referred to in the Ministerial Decree:

- Standard UNI EN 1594

- Standard UNI EN 14141 and complementary standards referred to therein

The valve types with related ND and construction requirements are indicated in Appendix 2.

## Ball valves

### OP ≤ 0.5 MPa (5 bar)

Reference legislation:

- Ministerial Decree of 16 April 2008

Technical standards referred to in the Ministerial Decree:

- Standard UNI 9165

- Standard UNI 9034

- Standard UNI 9734 and complementary standards referred to therein

or:

- Standard UNI EN 12007-1

- Standard UNI EN 12007-3

- Standard UNI EN 13774 and complementary standards referred to therein

The valve types with related ND and construction requirements are indicated in Appendix 6 and Appendix 7.

### 0.5 MPa (5 bar) ≤ OP ≤ 1.6 MPa (16 bar)

Reference legislation:

- Ministerial Decree of 17 April 2008

Technical standards referred to in the Ministerial Decree:

- Standard UNI EN 12007-1

- Standard UNI EN 12007-3

- Standard UNI EN 13774 and complementary standards referred to therein

The valve types with related ND and construction requirements are indicated in the following Appendices: Appendix 3, Appendix 4, Appendix 8, Appendix 10, Appendix 11, Appendix 12.

### OP ≥ 1.6 MPa (16 bar)

Reference legislation:

- Ministerial Decree of 17 April 2008

Technical standards referred to in the Ministerial Decree:

- Standard UNI EN 1594

- Standard UNI EN 14141 and complementary standards referred to therein

The valve types with related ND and construction requirements are indicated in the following Appendices: Appendix 5, Appendix 9, Appendix 13.

## Butterfly valves

Reference legislation:

- Ministerial Decree of 16 April 2008

Technical standards referred to in the Ministerial Decree:

- Standard UNI 9034

- Standard UNI EN 593

- Standard UNI 11354

- Standard UNI EN 13774 and complementary standards referred to therein

The valve types with related ND and construction requirements are indicated in Appendix 14 and must be supplied pre-assembled as shown in the figure provided therein.

## Body material

The quality of the material constituting the body of each individual valve covered by this Technical Specification must comply with the applied Standards.

In addition, for butt-weld valves, the material of the body must be compatible for welding with the piping material indicated in point 6.6.

## Butt-weld body ends

All butt-weld valves must be supplied with the ends tapered so that they can be welded during installation (Figure 1). The technical information required for the tapering is provided below.

### Tapering of valve body end

Figure 1 - Indicative representation

- Plug valves

The butt-weld valves shown in the relevant appendices must be tapered in accordance with UNI EN 12627 or equivalent.

- Ball valves

The butt-weld valves shown in the relevant appendices must be tapered in accordance with the technical reference standard applied:

- UNI 9734

- UNI EN 12627

- Butterfly valves

The flange ends applied to the butt-weld valves shown in the relevant appendices, must comply with UNI EN 1092-1.

## Characteristics of pipes used by Italgas Reti

Since, due to specific technical or supply requirements, the pipes indicated below may be subject to changes in their dimensional characteristics, it is Italgas Reti's responsibility to inform the Supplier of any variations at the order phase.

### Pipes used by ITALGAS RETI for MOP ≤ 1.2 MPa (12 bar)

For this pressure class, ITALGAS RETI uses steel pipes conforming to UNI EN ISO 3183, material grade PSL1, in the construction of its distribution networks:

- Symbolic designation L210

- Numerical designation 1.8713

- Rt0.5 = 210 N/mm²

The ends of the pipes are prepared in accordance with the above-mentioned standard.

The dimensional characteristics of the pipes are shown below in Table 1.

- Table 1 - Pipes for OP ≤ 1.2 MPa

- NOTES:

  - Tolerances on the outer diameter (OD) of the pipe end (taken from standard UNI EN ISO 3183):

- Table 2 - Tolerances on outer diameter OD

| - OD - (mm) | - Diameter tolerances - (mm) |  |  |  |
| --- | --- | --- | --- | --- |
|  | - Pipe (except ends) |  | - Pipe end |  |
|  | - Seamless pipe | - Welded pipe | - Seamless pipe | - Welded pipe |
| - OD < 60.3 | - from -0.8 to +0.4 |  |  |  |
| - 60.3 ≤ OD ≤ 168.3 | - ± 0.0075 OD |  | - from -0.4 to +1.6 |  |
| - 168.3 < OD ≤ 610 | - ± 0.0075 OD | - ± 0.0075 OD, - but maximum of ±3.2 | - ± 0.005 OD, - but maximum of ±1.6 |  |

  - Pipe end thickness tolerances (taken from UNI EN ISO 3183):

- Table 3 - End Thickness Tolerances

| Thickness T (mm) | Tolerances (mm) |
| --- | --- |
| Seamless pipe |  |
| T ≤ 4.0 | +0.6 -0.5 |
| 4.0 < T < 25.0 | + 0.15 T -0.125 T |
| Welded pipe |  |
| T ≤ 5.0 | ± 0.5 |
| 5.0 < T < 15.0 | ± 0.1 T |

### Pipes used by ITALGAS RETI for MOP  1.2 MPa (12 bar) and ≤ 7.5 MPa (75 bar)

For this pressure class, ITALGAS RETI uses steel pipes conforming to UNI EN ISO 3183, material grade PSL2, in the construction of its distribution networks:

- Alphanumeric designation L360N

- Numerical designation: 1.8793

- Rt0.5 = 360 N/mm²

The ends of the pipes are prepared in accordance with the above-mentioned standard.

The dimensional characteristics of the pipes are shown below in Table 4.

Table 4 - Pipes for 1.2 MPa < OP ≤ 7.5 MPa

- NOTES:

- Tolerances on the outer diameter (OD) of the pipe end (taken from standard UNI EN ISO 3183):

See Table 2, paragraph 6.6.1 of this specification.

- Pipe end thickness tolerances (taken from UNI EN ISO 3183):

- See Table 3, paragraph 6.6.1 of this specification.

## Operating device

In addition to the relevant characteristics provided for in the reference standards mentioned in this specification, all valves must be equipped with an operating element in accordance with UNI EN 12570 for all cases covered by this standard.

### Fixed operating element

Direct operation, by means of lever or reducer with handwheel, as indicated in the various appendices.

### Removable operating element

In the case of the supply of removable operating elements, the following requirements and technical characteristics must be met.

- T-spanner

Used to manoeuvre plug and ball valves for direct burial, fitted with a 22x22 mm connection for square head (see Appendices 1 - 2 - 3 - 4 - 5).

- Detachable reducer

Used to operate ball valves for direct burial, equipped with a flange connection that can be coupled with the valve flanges shown in Appendices 3 and 4.

### Operating device extensions

The dimensions of the valve operating device extensions, for direct burial, indicated in the relevant appendices, must provide for a laying depth of 1.10 m from the top line of the pipe on which the valves are to be assembled.

In the event that installations with different laying depths are required, Italgas Reti is responsible for informing the Supplier of the appropriate changes during the order phase.

## Position indicator (Obturator position)

On all valve types covered by this specification, an indicator showing the position of the obturator in both open and closed state must always be visible on the outside of the valve. All valves must therefore be provided with a durable (e.g. by engraving or other technical solutions) 'open' and 'closed' indicator on the reducer or square head.

## Protective coating

The protective coating of the valves must meet the characteristics described in the following points; other equivalent and durable treatments are permitted, provided they are approved by Italgas Reti. Paint must be applied after a suitable surface preparation, in accordance with Standard UNI EN ISO 8504, to ensure proper adhesion between the applied product and the metal substrate.

### Ball/Plug valves for underground use

The body and column of the valves indicated from Appendix 1 to Appendix 5 must be treated with thick epoxy resin paint suitable for underground use (HEMPEL, CARBOLINE, JOUTUN, INTERNATIONAL PAINT products, etc.) or equivalent materials for both mechanical and corrosion resistance.

### Ball valves for atmospheric or manhole use

Valves indicated from Appendix 6 to Appendix 11 must be treated with materials which are both mechanically and corrosion-resistant such as, for example:

- primer: galvanising or nitrosynthetic anti-rust product;

- top coat: polyurethane-based paint or nitro aluminium paint.

### Butterfly valves

The valves in Appendix 12 must be treated as follows:

- Above-ground service:

- primer:		galvanising or nitrosynthetic anti-rust product

- top coat: polyurethane-based paint or nitro aluminium paint

- Underground service:

These must be treated with thick epoxy resin paint suitable for underground use (HEMPEL, CARBOLINE, JOTUN, INTERNATIONAL PAINT products, etc.) or equivalent materials for both mechanical and corrosion resistance.

## Technical assessment

In relation to Legislative Decree 81 of 9 April 2008, as amended and supplemented, Italgas Reti reserves the right, in its evaluation of the use of the proposed products, to consider the operational consequences deriving from the conditions of use of the equipment as set out by the Supplier in the "Use and Maintenance Manual".

# MARKING

All valves must be marked with at least the following information:

- Supplier Logo

- Nominal diameter and end type

- Pressure class

- Base body material

In addition, all valves must be legibly and permanently marked with the mandatory markings specified by the relevant reference standards applied.

Valves within the scope of the:

- Italian Legislative Decree no. 85 of 19 May 2016.

- Italian Legislative Decree no. 93 of 25 February 2000, as amended

must be marked in accordance with the decrees, supplementing the markings if the valves fall within the scope of both decrees.

In any case, all specifications contained in any further standards that take into account partial constructional aspects relating to the valves described in this technical specification and that require other mandatory markings must be taken into account.

All markings must be positioned in accordance with UNI EN 19 wherever possible.

# TYPE TEST

During the design phase of the product, it shall be the Supplier's responsibility to carry out at recognised laboratories or directly at the Supplier's premises all the "Type Tests" required by the reference standards and/or the Supplier's own design standards and the standards referred to therein, to verify the intended end use of the product.

# TEST CONDITIONS

## Right of the Client

Italgas Reti reserves the right:

- To be present with its own Inspectors and/or Inspection Companies appointed by the same to carry out tests/checks c/o your plant and at your care and expense, to check the constructive and functional compliance of the materials in accordance with the specifications and/or reference standards.

- To verify, upon receipt and/or under actual conditions of use, the perfect compliance of the goods with the functional technical characteristics expressly indicated in the Contract.

It remains understood that the favourable outcome of our Inspection and checking of the materials shall not release you in any way from your responsibilities and obligations arising from every individual Contract.

## Tests and inspections

The tests and inspections to be carried out by the Supplier during the valve manufacturing process include at least the following:

- Pressure tests on body and seals according to the requirements of API 6D, UNI EN 12266 or UNI 9734 depending on the applicable reference standard;

- Visual and dimensional inspections;

- Non-destructive testing with magnetic particles in accordance with UNI EN ISO 17638 or penetrant liquid in accordance with UNI EN ISO 3452, on the welds of welded-body valves:

- Paint inspections:

  - Surface preparation in accordance with UNI EN ISO 8504;

  - Roughness control in accordance with UNI EN ISO 8503;

  - Thickness control according to ISO 19840 or equivalent standard.

# CONDITIONS OF SUPPLY

All valves supplied must be ready for installation, with the obturator positioned at maximum opening, and must be coated with a layer of suitable protective paint.

All valves supplied must be fitted with suitable end caps to prevent foreign bodies from entering and any butt-weld ends from being accidentally damaged.

# DOCUMENTATION REQUIRED FROM THE SUPPLIER

## Supplier

The potential Supplier must be qualified as an ITALGAS Supplier.

## Documents to be submitted

The potential Supplier must submit to the PROMA/CMMAT Department the “Declaration of Conformity” with this technical specification and any specific documents (legislative provisions, applied standards, etc.) to which the supplier refers for the design and construction of the product, in accordance with the requirements of UNI CEI EN ISO/IEC 17050-1 (see the example in APPENDIX 15 to this technical specification).

## Test Documentation

The Supplier must issue a “type 3.1” Inspection and Material Certificate in accordance with UNI EN 10204, which states that the products provided are compliant with the requirements of these specifications and which provides the test results.

Registration of the full production/test documentation completed by the Supplier must be kept (on the basis of legal provisions) for 10 years under its responsibility, and must be made available whenever requested by the Client.

## Supply Documentation

        - Documents compliant with Legislative Decree no. 286 of 21 November 2005, as amended

        - "EU Declarations of Conformity" in relation to its products if they are covered by the relevant "Product Directives";

        - Installation, operation and maintenance manuals accompanying the products

## Right of the Client

It is Italgas Reti's right, for each purchase order, to request from the Supplier:

- Further technical and/or graphic documentation,

- additional laboratory and/or field tests,

in order to verify the conformity of the proposed products with this technical specification and the cited standards to which reference is made.

# REFERENCE STANDARDS

- Legislative Decree No. 85 of 19 May 2016 - "Implementation of Directive 2014/34/EU on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres".

- Legislative Decree No. 233 of 12 June 2003 - 'Implementation of Directive 1999/92/EC on minimum requirements for improving the safety and health protection of workers exposed to the risk of explosive atmospheres'.

- Italian Legislative Decree no. 93 of 25 February 2000, as amended - “Implementation of Directive 97/23/EC on pressure equipment and Directive 2014/68/EU on the harmonisation of the laws of the Member States relating to the making available on the market of pressure equipment (recast), providing for its repeal”.

- Italian Legislative Decree no. 81 of 9 April 2008, as amended - “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”.

- Italian Legislative Decree no. 152 of 3 April 2006, as amended “Environmental standards”.

- Italian Legislative Decree no. 286 of 21 November 2005, as amended “Provisions for the regulatory reorganisation of the regulated liberalisation of the road haulage business”.

- Ministerial Decree of 16 April 2008 - “Technical regulations for the design, construction, testing, operation and supervision of works and distribution systems and direct lines for natural gas with a density not exceeding 0.8”.

- Ministerial Decree of 17 April 2008 - “Technical regulations for the design, construction, testing, operation and supervision of works and plants for the transmission of natural gas with a density not exceeding 0.8”.

- UNI 9734 - “Shut-off devices for gas pipelines. Steel valves with ball obturator”.

- UNI 9034 - “Gas distribution pipelines with maximum operating pressure (MOP) not exceeding 0.5 MPa (5 bar) - Materials and jointing systems”.

- UNI 9165 - "Gas distribution networks - Pipelines with maximum operating pressure (MOP) of up to 5 bar - Design, construction, testing, operation, maintenance and rehabilitation".

- UNI CEI EN ISO/IEC 17050-1 - "Conformity assessment - Supplier's declaration of conformity - Part 1: General requirements"

- UNI EN 19 - “Industrial valves. Marking of metal valves”

- UNI EN 12982 - "Industrial valves - Face-to-face and centre-to-face dimension for butt-weld end valves".

- UNI EN 12266-1 - "Industrial valves - Testing of metallic valves - Pressure tests, test procedures and acceptance criteria - Mandatory requirements".

- UNI EN 558 - “Industrial valves. Face-to-face and centre-to-face dimensions of metal valves for use in flanged pipe systems. PN- and class-designated valves”

- UNI EN 593 - “Industrial valves. Metallic butterfly valves”

- UNI 11354 - "Shut-off devices for gas distribution and/or transportation networks - Butterfly valves”.

- UNI EN 1092-1 - "Flanges and their joints. Circular flanges for pipes, valves, fittings and accessories PN-designated - Part 1: Steel flanges”

- UNI EN ISO 3183 - “Petroleum and natural gas industries - Steel pipe for pipeline transportation systems”.

- UNI EN ISO 17638 - "Non-destructive testing of welds - Magnetic particle testing”.

- UNI EN ISO 3452 - “Non-destructive testing - Penetrant testing”.

- UNI EN ISO 8504 - “Preparation of steel substrates before application of paints and related products - Surface preparation methods”.

- UNI EN ISO 8503 - “Preparation of steel substrates before application of paints and similar products - Surface roughness characteristics of blast cleaned steel substrates”.

- ISO 19840 - "Paints and varnishes - Corrosion protection of steel structures by protective paint systems - Measurement of, and acceptance criteria for, the thickness of dry films on rough surfaces".

- UNI EN 12570 - “Industrial valves - Method for sizing the operating element”.

- UNI EN 12627 - “Industrial valves. Butt weld ends for steel valves”.

- UNI CEI EN ISO 80079-36 - “Explosive atmospheres - Part 36: Non-electrical equipment for explosive atmospheres - Basic method and requirements”

- UNI EN 13774 - "Valves for gas distribution systems with maximum operating pressure less than or equal to 16 bar. Performance requirements.”

- UNI EN 14141 - “Valves for natural gas transportation in pipelines - Performance requirements and tests'.

- UNI EN 12007-1 - "Gas infrastructure - Pipelines for maximum operating pressure up to and including 16 bar - Part 1: General Functional Requirements”.

- UNI EN 12007-3 - "Gas infrastructure - Pipelines for maximum operating pressure up to and including 16 bar - Part 3: Specific functional requirements for steel”.

- UNI EN 1594 - "Gas infrastructure - Pipelines for maximum operating over 16 bar - Functional requirements”.

- UNI EN 228-1 - "Pipe threads where pressure-tight joints are not made on the threads" - Dimensions, tolerances and designation".

- API SPEC 6D - “Specification for Pipeline Valves (Gate, Plug, Ball, and Check Valves)”

- ASME B 16.10 - “Face to Face and End to End Dimensions of Valves”

- ASME B 16.25 - “Buttwelding Ends”

- ASME B 16.5 - “Pipe Flanges and Flanged Fittings”

# APPENDICES

- APPENDIX 1 - "Inverted plug valve, butt-weld end, for direct burial, with manhole operation, ANSI 150"

- APPENDIX 2 - "Inverted plug valve, butt-weld end, for direct burial, with manhole operation, ANSI 300"

- APPENDIX 3 - "Floating ball valve, butt-weld end, for direct burial, with manhole operation, ANSI 150"

- APPENDIX 4 - "Fixed ball valve, butt-weld end, for direct burial, with manhole operation, ANSI 150"

- APPENDIX 5 - "Floating ball valve, butt-weld end, for direct burial, with manhole operation, ANSI 300"

- APPENDIX 6 - "Floating ball valve, butt-weld end, ANSI 150"

- APPENDIX 7 - "Floating ball valve, butt-weld and threaded end, ANSI 150"

- APPENDIX 8 - "Floating ball valve, BW/RF end, ANSI 150"

- APPENDIX 9 - "Floating ball valve, BW/RF end, ANSI 300"

- APPENDIX 10 - "Floating ball valve, with flanged end, ANSI 150"

- APPENDIX 11 - "Fixed ball valve, with flanged end, ANSI 150"

- APPENDIX 12 - "Floating ball valve, with flanged end, ANSI 300"

- APPENDIX 13 - "Floating ball valve, with flanged end, ANSI 600"

- APPENDIX 14 - “Steel butterfly valve, butt-weld end”

- APPENDIX 15 - “Sample declaration of conformity with this technical specification”

## Appendix 1

INVERTED PLUG VALVE, BUTT-WELD END, FOR DIRECT BURIAL, WITH MANHOLE OPERATION, ANSI 150

Material code 4010202515/A.

(*)

Figure 1

HAZARDOUS PLACE	: zone 1 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 2G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP):	0.5 MPa (5 bar)

ND		: nominal diameter

OBTURATOR	: with Venturi flow

FACE-TO-FACE AND CENTRE-TO-FACE* (A)	: complies with the applied reference standards:

- ASME B16.10, if API SPEC 6D Standard is applied

- UNI EN 12982, if UNI EN standards are applied

ENDS	: see point 6.5.

OPERATION TYPE	: operated by fixed manual reducer, with detachable spanner

PROTECTIVE COATING: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | H mm | E (1) mm | Mass (2) kg |
| --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |
| 40102025150 | 12 | 300 | 1060 | 22 x 22 | 350 |
| 40102025151 | 14 | 350 | 1080 | 22 x 22 | 435 |
| 40102025152 | 16 | 400 | 1100 | 22 x 22 | 760 |
| 40102025154 | 20 | 500 | 1160 | 22 x 22 | 1175 |

(1)	Square head with ~ 25 mm height for use of T-spanners

(2)	Indicative

## Appendix 2

INVERTED PLUG VALVE, BUTT-WELD END, FOR DIRECT BURIAL, WITH MANHOLE OPERATION, ANSI 300

Material code 4010202516.

(*)

Figure 1

HAZARDOUS PLACE	: zone 1 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 2G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	: 2.4 MPa (24 bar)

ND	: nominal diameter

OBTURATOR	:	with Venturi flow

FACE-TO-FACE AND CENTRE-TO-FACE* (A)	: according to UNI EN 12982

ENDS	: see point 6.5.

OPERATION TYPE	: operated by fixed manual reducer, with detachable spanner

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | H mm | E (1) mm | Mass (2) kg |
| --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |
| 40102025161 | 6 | 150 | 990 | 22 x 22 | 156 |
| 40102025162 | 8 | 200 | 1010 | 22 x 22 | 225 |
| 40102025163 | 10 | 250 | 1040 | 22 x 22 | 320 |
| 40102025164 | 12 | 300 | 1060 | 22 x 22 | 410 |
| 40102025165 | 14 | 350 | 1080 | 22 x 22 | 525 |
| 40102025166 | 16 | 400 | 1100 | 22 x 22 | 745 |
| 40102025168 | 20 | 500 | 1160 | 22 x 22 | 1385 |

(1)	Square head with ~ 25 mm height for use of T-spanners

(2)	Indicative

## Appendix 3

FLOATING BALL VALVE, BUTT-WELD END, FOR DIRECT BURIAL, WITH MANHOLE OPERATION, ANSI 150

Material code 4010207152/5.

(*)

Figure 1

| See Figure 3 |  |
| --- | --- |
| Figure 2 | Figure 3 - Valve/Detachable Reducer Coupling |

## Appendix 3

HAZARDOUS PLACE	: zone 1 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 2G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	: 1.2 MPa (12 bar)

ND	: nominal diameter

OBTURATOR	: floating ball

DOO	: diameter obturator opening according to the applied standard (see point 6.2.)

FACE-TO-FACE AND CENTRE-TO-FACE* (A)	: according to UNI EN 12982

ENDS	: See point 6.5.

OPERATION TYPE	: for ND  6" x 4"	: direct actuation with detachable spanner (Figure 1)

for ND 8" x 6"	: operated by means of manual, detachable reducer with handwheel (Figure 2) or crank

COUPLING FLANGE TO REDUCER	: Figure 3

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | DOO mm | H mm | E (1) mm | Mass (3) kg |
| --- | --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |  |
| 40102071520 | 1 ½ | 40 | full | 995 | 22 x 22 | 13 |
| 40102071521 | 2 | 50 | full | 995 | 22 x 22 | 18 |
| 40102071523 | 3 | 80 | full | 1005 | 22 x 22 | 30 |
| 40102071524 | 4 | 100 | full | 1025 | 22 x 22 | 44 |
| 40102071556 | 6 x 4 | 150 x 100 | reduced | 1055 | 22 x 22 | 61 |
| 40102071558 | 8 x 6 | 200 x 150 | reduced | 1090 | 36 x 27 (2) | 144 |

(1)	Square head with a useful height of:

- ~ 25 mm for valves with T-spanner;

- 30 mm for valve/detachable reducer coupling

(2)	Dimensions refer to the square head of the valve/detachable reducer coupling

(3)	Indicative

## Appendix 4

FIXED BALL VALVE, BUTT-WELD END, FOR DIRECT BURIAL, WITH MANHOLE OPERATION, ANSI 150

Material code 4010207156/A.

| (*) | See Figure 3 |  |  |
| --- | --- | --- | --- |
| Figure 1 | Figure 2 |  |  |
| Figure 3 - Valve/Detachable Reducer Coupling |  | Figure 4 |  |

## Appendix 4

HAZARDOUS PLACE	: zone 1 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 2G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	:	1.2 MPa (12 bar)

ND	: nominal diameter

OBTURATOR	: trunnion-mounted

DOO	: diameter obturator opening according to the applied standard (see point 6.2.)

FACE-TO-FACE AND CENTRE-TO-FACE* (A)	: according to UNI EN 12982

ENDS	: see point 6.5.

TYPE OF OPERATION	: for ND 10" x 8" : operated by detachable reducer with handwheel or crank (Figures 1- 2- 3)

for ND  12" x 10"	: operated by fixed reducer with detachable spanner (Figure 4)

COUPLING FLANGE TO REDUCER	: see Figure 3

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | DOO mm | H mm | E (1) mm | Mass (3) kg |
| --- | --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |  |
| 40102071560 | 10 x 8 | 250 x 200 | reduced | 1110 | 36 x 27 (2) | 230 |
| 40102071562 | 12 x 10 | 300 x 250 | reduced | 1140 | 22 x 22 | 420 |
| 40102071564 | 14 x 10 | 350 x 250 | reduced | 1150 | 22 x 22 | 480 |
| 40102071565 | 16 x 12 | 400 x 300 | reduced | 1150 | 22 x 22 | 660 |

(1)	Square head with a useful height of:

- ~ 25 mm for valves with T-spanner;

- 30 mm for valve/detachable reducer coupling

(2)	Dimensions refer to the square head of the valve/detachable reducer coupling

(3)	Indicative

## Appendix 5

FLOATING BALL VALVE, BUTT-WELD END, FOR DIRECT BURIAL, WITH MANHOLE OPERATION, ANSI 300

Material code 4010207157.

(*)

Figure 1

HAZARDOUS PLACE	: zone 1 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 2G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	:2.4 MPa (24 bar)

ND	: nominal diameter

OBTURATOR	: floating ball

DOO	: diameter obturator opening according to the applied standard (see point 6.2.)

FACE-TO-FACE AND CENTRE-TO-FACE* (A)	: according to UNI EN 12982

ENDS	: see point 6.5.

OPERATION TYPE	: direct actuation with detachable spanner

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | DOO mm | H mm | E (1) mm | Mass (2) kg |
| --- | --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |  |
| 40102071574 | 3 | 80 | full | 1005 | 22 x 22 | 30 |
| 40102071575 | 4 | 100 | full | 1025 | 22 x 22 | 44 |

(1)	Square head with ~ 25 mm height for use of T-spanners

(2)	Indicative

## Appendix 6

FLOATING BALL VALVE, BUTT-WELD END, ANSI 150

Material code 40102071566

Figure 1

HAZARDOUS PLACE	: zone 1 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 2G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	:	0.5 MPa (5 bar)

ND	: nominal diameter

OBTURATOR	: floating ball

DOO	: diameter obturator opening according to the applied standard (see point 6.2.)

FACE-TO-FACE AND CENTRE-TO-FACE	: according to UNI EN 12982

ENDS	: see point 6.5.

OPERATION TYPE	: direct actuation with lever

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | DOO mm | A mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |
| 40102071566 | ¾ | 20 | full | 152 | 2 |

(1)	Indicative

## Appendix 7

FLOATING BALL VALVE, BUTT-WELD AND THREADED, ANSI 150

Material code 40102071567

Figure 1

HAZARDOUS PLACE	: zone 1 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 2G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	: 0.5 MPa (5 bar)

ND	: nominal diameter

OBTURATOR	: floating ball

DOO	: diameter obturator opening according to the applied standard (see point 6.2.)

FACE-TO-FACE AND CENTRE-TO-FACE	: according to UNI EN 12982 (by analogy of construction to the valve with both ends butt-weld)

ENDS	: butt-weld : see point 6.5.

: threaded : in accordance with UNI EN ISO 228-1

OPERATION TYPE	: direct actuation with lever

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | DOO mm | A mm | Mass (1) Kg |
| --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |
| 40102071567 | ¾ | 20 | full | 152 | 2 |

(1)	Indicative

## Appendix 8

FLOATING BALL VALVE, WITH BW/RF END, ASME 150

Material code 4010207175.

Figure 1

HAZARDOUS PLACE	: zone 1 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 2G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	: 1.2 MPa (12 bar)

ND	: nominal diameter

OBTURATOR	: floating ball

DOO	: diameter obturator opening according to the applied standard (see point 6.2.)

FACE-TO-FACE AND CENTRE-TO-FACE	: according to UNI EN 558

ENDS	: flanged side	:	stepped flange according to ASME B16.5, class 150 RF

butt-weld side	:	see point 6.5.

OPERATION TYPE	: direct actuation with lever

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | DOO mm | A mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |
| 40102071755 | 1 ½ | 40 | reduced | 165 | 4.2 |
| 40102071756 | 2 | 50 | reduced | 178 | 8 |
| 40102071758 | 3 | 80 | reduced | 203 | 20 |

(1)	Indicative

## Appendix 9

FLOATING BALL VALVE, WITH BW/RF END, ASME 300

Material code 4010207176.

Figure 1

HAZARDOUS PLACE	: zone 1 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 2G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	: 2.4 MPa (24 bar)

ND	: nominal diameter

OBTURATOR	: floating ball

DOO	: diameter obturator opening according to the applied standard (see point 6.2.)

FACE-TO-FACE AND CENTRE-TO-FACE	:	according to UNI EN 558

ENDS	: flanged side	: stepped flange according to ASME B 16.5, class 300 RF

butt-weld side	:	see point 6.5.

OPERATION TYPE	: direct actuation with lever

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | DOO mm | A mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |
| 40102071765 | 1 ½ | 40 | reduced | 190 | 8.5 |
| 40102071766 | 2 | 50 | reduced | 216 | 13.5 |
| 40102071768 | 3 | 80 | reduced | 283 | 25 |

(1)	Indicative

## Appendix 10

FLOATING BALL VALVE WITH FLANGED ENDS, ASME 150

Material code 4010207183/8.

| Figure 1 | Figure 2 |
| --- | --- |

HAZARDOUS PLACE	: zone 1 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 2G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	: 1.2 MPa (12 bar)

ND	: nominal diameter

OBTURATOR	: floating ball

DOO	: diameter obturator opening according to the applied standard (see point 6.2.)

FACE-TO-FACE AND CENTRE-TO-FACE	: according to UNI EN 558

ENDS	: stepped flange according to ASME B 16.5, class 150 RF

OPERATION TYPE	: for ND  8" x 6"	: direct actuation with lever (Figure 1)

for ND  8"	: operated by fixed reducer with handwheel (Figure 2)

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | DOO mm | A mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |
| 40102071832 | 1 ½ | 40 | full | 165 | 11.3 |
| 40102071834 | 2 | 50 | full | 178 | 13 |
| 40102071836 | 3 | 80 | full | 203 | 25 |
| 40102071837 | 4 | 100 | full | 229 | 41 |
| 40102071881 | 6 x 4 | 150 x 100 | reduced | 267 | 58 |
| 40102071838 | 6 | 150 | full | 394 | 118 |
| 40102071882 | 8 x 6 | 200 x 150 | reduced | 292 | 118 |
| 40102071839 | 8 | 200 | full | 457 | 149 |
| 40102071883 | 10 x 8 | 250 x 200 | reduced | 330 | 168 |

(1)	Indicative

## Appendix 11

FIXED BALL VALVE, WITH FLANGED ENDS, ASME 150

Material code 4010207183/8/A.

Figure 1

HAZARDOUS PLACE	: zone 2 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 3G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	: 1.2 MPa (12 bar)

ND	: nominal diameter

OBTURATOR	: trunnion-mounted

DOO	: diameter obturator opening according to the applied standard (see point 6.2.)

FACE-TO-FACE AND CENTRE-TO-FACE	: according to UNI EN 558

ENDS	: stepped flange according to ASME B 16.5, class 150 RF

OPERATION TYPE	: operated by fixed reducer, with handwheel

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | DOO mm | A mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |
| 40102071840 | 10 | 250 | full | 533 | 454 |
| 40102071884 | 12 x 10 | 300 x 250 | reduced | 610 | 513 |
| 40102071830 | 12 | 300 | full | 610 | 680 |
| 40102071885 | 14 x 10 | 350 x 250 | reduced | 686 | 561 |
| 40102071831 | 14 | 350 | full | 686 | 882 |
| 40102071833 | 16 | 400 | full | 762 | 1050 |

(1)	Indicative

## Appendix 12

FLOATING BALL VALVE, WITH FLANGED ENDS, ASME 300

Material code 4010207184/7.

Figure 1

HAZARDOUS PLACE	: zone 1 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 2G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	: 1.2 MPa (12 bar)

ND	: nominal diameter

OBTURATOR	: floating ball

DOO	: diameter obturator opening according to the applied standard (see point 6.2.)

FACE-TO-FACE AND CENTRE-TO-FACE	: according to UNI EN 558

ENDS: stepped flanges: comply with standard ASME B 16.5, class 300

OPERATION TYPE	: direct actuation with lever

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | DOO mm | A mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |
| 40102071842 | 1 ½ | 40 | full | 190 | 15.2 |
| 40102071844 | 2 | 50 | full | 216 | 21 |
| 40102071846 | 3 | 80 | full | 283 | 46 |
| 40102071847 | 4 | 100 | full | 305 | 81 |
| 40102071872 | 6 x 4 | 150 x 100 | reduced | 403 | 78 |

(1)	Indicative

## Appendix 13

FLOATING BALL VALVE, WITH FLANGED ENDS, ANSI 600

Material code 4010207185/6.

Figure 1

HAZARDOUS PLACE	: zone 2 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 3G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	: 7.5 MPa (75 bar)

ND	: nominal diameter

OBTURATOR	: floating ball

DOO	: diameter obturator opening according to the applied standard (see point 6.2.)

FACE-TO-FACE AND CENTRE-TO-FACE	: according to UNI EN 558

END	: stepped flanges: comply with standard ANSI B 16.5, class 600

OPERATION TYPE	: direct actuation with lever

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | DOO mm | A mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |
| 40102071851 | 1 ½ | 40 | full | 241 | 19 |
| 40102071852 | 2 | 50 | full | 292 | 25.5 |
| 40102071854 | 3 | 80 | full | 356 | 63 |
| 40102071866 | 6 x 4 | 150 x 100 | reduced | 559 | 122 |

(1)	Indicative

## Appendix 14

STEEL, BUTTERFLY VALVE,

BUTT-WELD ENDS

Material code 401020725.

Figure 1

HAZARDOUS PLACE	: zone 1 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 2G or higher), see point 5.2.

MAXIMUM OPERATING PRESSURE (MOP)	: 0.05 MPa (0.5 bar)

ND	: nominal diameter

OD	: outer diameter

VALVE CLASS: NP 16

BODY	: wafer type (see Fig. 2 of UNI EN 593)

FACE-TO-FACE AND CENTRE-TO-FACE	: according to UNI EN 558

CONNECTION	: assembled with flanges

FLANGE CLASS:	PN 16 according to UNI EN 1092-1

OPERATION TYPE	: direct actuation with detachable lever

PROTECTIVE COATING	: see point 6.9.

Table 1 - Dimensional characteristics

| Material code | ND |  | A mm | B mm | C mm | OD mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | inches | mm |  |  |  |  |  |
| 40102072536 | 2 | 50 | 43 | 45 | 133 | 60.3 | 11 |
| 40102072541 | 3 | 80 | 46 | 50 | 146 | 88.9 | 16 |
| 40102072543 | 4 | 100 | 52 | 52 | 156 | 114.3 | 21 |
| 40102072545 | 6 | 150 | 46 | 55 | 166 | 168.3 | 33 |

(1)	Indicative

## Appendix 15

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN ISO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

(4)	The following products manufactured by us:

| Our material code (5) | Italgas Reti material code (6) |
| --- | --- |
| xxx | 40102072536 |
| xxx | xxx |

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(7)	S.T.V.F.C. 2000300	STEEL VALVES FOR GAS PIPELINES	Edition 1 of 15/06/2017

Additional information:

(8) 	...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(9) 	.............................................................		......................................................................................................................

(Name and position) 						(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- The “subject” must be unambiguously described so that the declaration of conformity can be referred to the subject in question.

- List all the products for which company use authorisation is being requested.

- For each individual product supplied, state the material code used by the Supplier.

- For each individual product supplied, please quote the material code assigned by Italgas Reti, which can be found in the Italgas Reti reference documents. If there are none, please contact SERTEC-NORM.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

Supplier means the party responsible for the design and construction of the products or its legal representative as defined in Legislative Decree no. 206 of 6 September 2005 as amended and supplemented. - "CONSUMER CODE" pursuant to Article 7 of Law no. 229 of 29 July 2003.