- “TECHNICAL SPECIFICATION FOR EVALUATION, SUPPLY AND TESTING”

- S.T.V.F.C. 176A300

Malleable cast iron fittings, galvanised

| Compiled by | SERTEC-NORM | TARANTINO ANDREA |
| --- | --- | --- |
| Checked by | SERTEC-NORM | VARESE ENRICO |
| Checked by | PROMA/CMMAT | FASSINO SILVIO |
| Checked by | HSEQ | BOLZONI GIANLUCA |
| Checked by | PROMA-MATMA | SCOTTO ENRICO |
| Approved by | SERTEC | COMAZZI MARCO |

SUMMARY

1	PRELIMINARY INFORMATION	4

1.1	Cancels and replaces	4

1.2	Reason for issue	4

1.3	Company departments mentioned in the document	4

1.4	Definitions	4

2	PURPOSE AND FIELD OF APPLICATION	4

2.1	Purpose	4

2.2	Field of application	4

3	SPECIFICATIONS	4

4	TECHNICAL CHARACTERISTICS	5

4.1	Material	5

4.2	Pressure range	5

4.3	Protective coating	5

4.4	Technical assessment	5

5	Marking	6

6	TYPE TEST	6

7	DOCUMENTATION REQUIRED FROM THE SUPPLIER	6

7.1	Supplier	6

7.2	documents to be submitted	6

7.3	Test Documentation	7

7.4	Supply Documentation	7

7.5	Right of the client	7

8	Test conditions	7

8.1	Tests and inspections	7

9	CONDITIONS OF SUPPLY	7

10	REFERENCE STANDARDS	8

11	APPENDICES	8

Appendix 1	9

Appendix 2	10

Appendix 3	11

Appendix 4	12

Appendix 5	13

Appendix 6	14

Appendix 7	15

Appendix 8	16

Appendix 9	17

Appendix 10	18

Appendix 11	19

Appendix 12	20

Appendix 13	21

Appendix 14	22

Appendix 15	23

Appendix 16	24

Appendix 17	24

Appendix 18	26

Appendix 19	27

Appendix 20	28

# PRELIMINARY INFORMATION

## Cancels and replaces

This specification cancels and replaces the Technical Specification 176A300, edition 1, dated 28.09.2004 – "Malleable cast iron fittings, galvanised".

## Reason for issue

The update of the Technical Specification 176A300 and its reissue in the form of Technical Specifications for Assessment, Supply and Testing (S.T.V.F.C.), became necessary as a result of:

- New legislative context;

- Issuance of new national and European standards (e.g. UNI, EN, etc.);

- Inclusion of Supply and Testing Criteria;

## Company departments mentioned in the document

- PROMA-CMMAT = Materials

- SERTEC = Technical Services

## Definitions

The technical definitions contained in this specification conform to those prescribed by the standards listed in section “Reference standards”.

# PURPOSE AND FIELD OF APPLICATION

## Purpose

To define the technical characteristics, the accompanying documentation, the criteria for supply and testing, and the procedures for carrying out the technical inspections to be performed for the approval for company use of galvanised, malleable cast iron fittings.

## Field of application

It applies whenever material covered by this specification must be authorised for company use, produced

by a new potential Supplier or by an existing one.

# SPECIFICATIONS

- These technical specifications must be understood as an integral part of the "ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS RETI."

- this specification contains the minimum technical requirements demanded by Italgas Reti based on the reference Legislative and Technical Standards;

- It is the Supplier's responsibility to ensure that the products supplied fully comply with the provisions of this technical specification and the applicable standards.

- If the products in question are supplied by an installer, the installer must document their compliance as required under “Documentation required from the Supplier”.

- It is the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. sharp edges, incorrect directions for use and maintenance, etc.), which may jeopardise the health and safety of the Client's workers in relation to the provisions of Legislative Decree no. 81/08, as amended and supplemented.

- For any technical and operational aspects that conflict with or are not mentioned in this technical specification but that nevertheless pertain to the design, installation, maintenance and use of the products themselves, it is the Supplier's responsibility to refer to the regulations in force.

# TECHNICAL CHARACTERISTICS

Malleable cast iron fittings must be manufactured, tested and certified in accordance with the requirements of:

- Ministerial Decree of 16 April 2008

- Standard UNI 9034

- Standard UNI EN 10242

The drawings contained in the various Appendices should be considered as a "standard model shown as an example", the specified dimensions and technical characteristics should, instead, be considered as binding.

## Material

The material of the fittings may be made of:

- Malleable cast iron with a white core;

- Malleable cast iron with a black core.

in accordance with Ministerial Decree of 16 April 2008, UNI 9034 and UNI EN 10242.

The technical characteristics of the material (e.g. mechanical properties, physical properties, chemical composition, technical reference standards, etc.) must be stated in the respective Material Certificates "type 3.1" in accordance with standard UNI EN 10204.

## Pressure range

The maximum operating pressure to which the fittings covered by this Specification are subjected is 0.05 MPa (0.5 bar).

## Protective coating

The pipes must be provided with a metal coating consisting of hot dip galvanisation. This coating must be manufactured in accordance with the requirements of standard UNI EN 10242, section 5.2.

## Technical assessment

In relation to Legislative Decree no. 81/08, as amended and supplemented, Italgas Reti reserves the right, in its evaluation of the use of the proposed products, to consider the operational consequences deriving from the conditions of use of the equipment as prescribed by the Supplier in the "Use and Maintenance Manual".

# Marking

Fittings must be marked legibly and with the indications required by UNI EN 10242, section 14.

# TYPE TEST

During the design phase of the product, it shall be the Supplier's responsibility to carry out at recognised laboratories or directly at the Supplier's premises all the "Type Tests" required by the reference standards and/or the Supplier's own design standards and the standards referred to therein, to verify the intended end use of the product.

# DOCUMENTATION REQUIRED FROM THE SUPPLIER

## Supplier

The potential Supplier must be qualified as an Italgas Supplier.

## documents to be submitted

The potential Supplier must submit the following documentation to the PROMA-CMMAT Department:

- “Declaration of Conformity” with this technical specification and any specific documents (legislative provisions, applied standards, etc.) to which the supplier refers for the design and construction of the product, in accordance with the requirements of UNI CEI EN ISO/IEC 17050-1 (see the example in APPENDIX 20 to this technical specification).

- Preliminary technical documentation describing the product, including information on the material, construction drawings, dimensional characteristics, tests and inspections required by the Supplier's standard, etc;

- Statement certifying ownership to market the product;

- Any list of references of the main customers using the proposed materials;

- Any product and process certifications issued by officially recognised bodies;

- any additional documentation deemed useful by the potential Supplier to better qualify the proposed product.

## Test Documentation

The Supplier must issue a “type 3.1” Inspection Certificate in accordance with UNI EN 10204, which states that the products provided are compliant with the requirements of these specifications and which provides the test results.

Registration of the full production/test documentation completed by the Supplier must be kept (on the basis of legal provisions) for 10 years under its responsibility, and must be made available whenever requested by the Client.

## Supply Documentation

  - Documents compliant with Legislative Decree no. 286 of 21 November 2005, as amended

  - “Type 3.1” Inspection and Material Certificates in accordance with UNI EN 10204;

  - Approved technical documentation (construction drawings, etc.) of the product.

## Right of the client

It is Italgas Reti's right, for each purchase order, to request from the Supplier:

- to produce further technical documentation and/or drawings,

- the performance of any additional laboratory and/or field tests,

in order to verify the conformity of the proposed products with this technical specification and the cited standards to which reference is made.

# Test conditions

Italgas Reti reserves the right:

- To be present with its own Inspectors and/or Inspection Companies appointed by the same to carry out tests/checks c/o your plant and at your care and expense, to check the constructive and functional compliance of the materials in accordance with the specifications and/or reference standards.

- To verify, upon receipt and/or under actual conditions of use, the perfect compliance of the goods with the functional technical characteristics expressly indicated in the Contract.

It remains understood that the favourable outcome of our Inspection and checking of the materials shall not release you in any way from your responsibilities and obligations arising from every individual Contract.

## Tests and inspections

In accordance with UNI EN 10242, section 11.

# CONDITIONS OF SUPPLY

Supplier's standards in accordance with Legislative Decree no. 152 of 3 April 2006, as amended

# REFERENCE STANDARDS

- Italian Legislative Decree no. 81 of 9 April 2008, as amended - “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”.

- Italian Legislative Decree no. 152 of 3 April 2006, as amended “Environmental standards”.

- Italian Legislative Decree no. 286 of 21 November 2005, as amended - “Provisions for the regulatory reorganisation of the regulated liberalisation of the road haulage business”.

- Ministerial Decree of 16 April 2008 - “Technical regulations for the design, construction, testing, operation and supervision of works and distribution systems and direct lines for natural gas with a density not exceeding 0.8”.

- UNI CEI EN ISO/IEC 17050-1 - "Conformity assessment - Supplier's declaration of conformity - Part 1: General requirements”.

- UNI 9034- “Gas distribution pipelines with maximum operating pressure (MOP) not exceeding 0.5 MPa (5 bar– Materials and jointing systems”.

- UNI EN 10242 - "Threaded pipe fittings in malleable cast iron".

# APPENDICES

- APPENDIX 1 - "90° male-female bend"

- APPENDIX 2 - "90° female-female bend"

- APPENDIX 3 - "90° male-female elbow"

- APPENDIX 4 - "90° female-female elbow"

- APPENDIX 5 - "90° male-female elbow"

- APPENDIX 6 - "45° male-female bend"

- APPENDIX 7 - "45° female-female bend"

- APPENDIX 8 - "Tee"

- APPENDIX 9 - "Reduction pitcher tee"

- APPENDIX 10 - “Cross"

- APPENDIX 11 - "Male-female reduction"

- APPENDIX 12 - "Male-female sleeve"

- APPENDIX 13 - "Right-thread sleeve"

- APPENDIX 14 - "Reduction nipple"

- APPENDIX 15 - "Nipple"

- APPENDIX 16 - "Plug"

- APPENDIX 17 - "Nut cap"

- APPENDIX 18 - "Flat-seat union"

- APPENDIX 19 - "Flat-seat union, male-female"

- APPENDIX 20 - “Sample declaration of conformity with this technical specification”

## Appendix 1

90° MALE-FEMALE BEND

Material code 336017610.

Figure 1 - Graphical representation

ND	: nominal pipe diameter

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | b mm | z mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- |
| 33601761010 | ¾ | 69 | 60 | 54 | 22.0 |
| 33601761012 | 1 | 85 | 75 | 68 | 36.5 |
| 33601761016 | 1 ½ | 116 | 105 | 97 | 77.0 |
| 33601761020 | 2 | 140 | 130 | 116 | 121.0 |
| 33601761026 | 3 | 205 | 190 | 175 | 320.0 |

(1) Indicative mass per 100 pieces

Description according to UNI EN 10242:

LARGE RADIUS BEND, MALE AND FEMALE, G4 (ex Fig. 1)

Table 17

## Appendix 2

90° FEMALE-FEMALE BEND

Material code 336017611.

Figure 1 - Graphical representation

ND	: nominal pipe diameter

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | z mm | Mass (1) kg |
| --- | --- | --- | --- | --- |
| 33601761110 | ¾ | 69 | 54 | 25.0 |
| 33601761112 | 1 | 85 | 68 | 41.0 |
| 33601761116 | 1 ½ | 116 | 97 | 86.5 |
| 33601761120 | 2 | 140 | 116 | 138.0 |
| 33601761126 | 3 | 205 | 175 | 350.0 |

(1) Indicative mass per 100 pieces

Description according to UNI EN 10242:

LARGE RADIUS BEND G1 (ex Fig. 2)

Table 17

## Appendix 3

90° MALE-FEMALE ELBOW

Material code 336017613.

Figure 1 - Graphical representation

ND	: nominal pipe diameter

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | b mm | z mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- |
| 33601761310 | ¾ | 33 | 43 | 18 | 23.5 |
| 33601761312 | 1 | 38 | 52 | 21 | 22.0 |
| 33601761314 | 1 1/4 | 45 | 60 |  | 39.2 |
| 33601761316 | 1 ½ | 50 | 65 | 31 | 41.0 |
| 33601761320 | 2 | 58 | 74 | 34 | 70.0 |
| 33601761326 | 3 | 78 | 98 | 48 | 160.0 |

(1) Indicative mass per 100 pieces

Description according to UNI EN 10242:

MALE AND FEMALE ELBOW A4 (ex Fig. 92)

Table 8

## Appendix 4

90° FEMALE-FEMALE ELBOW

Material code 336017614.

Figure 1 - Graphical representation

ND	: nominal pipe diameter

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | z mm | Mass (1) kg |
| --- | --- | --- | --- | --- |
| 33601761410 | ¾ | 33 | 18 | 13.0 |
| 33601761412 | 1 | 38 | 21 | 20.5 |
| 33601761412 | 1 1/4 | 45 | 45 | 40.6 |
| 33601761416 | 1 ½ | 50 | 31 | 40.0 |
| 33601761420 | 2 | 58 | 34 | 63.0 |
| 33601761426 | 3 | 78 | 48 | 140.0 |

(1) Indicative mass per 100 pieces

Description according to UNI EN 10242:

ELBOW A1 (ex Fig. 90)

Table 8

## Appendix 5

90° MALE-FEMALE REDUCTION ELBOW

Material code 336017616.

Figure 1 - Graphical representation

ND	: nominal pipe diameter

Table 1 - Material code and dimensions

| Material code | ND x nd inches | a mm | c mm | z1 mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- |
| 33601761615 | 1 x ¾ | 35 | 46 | 18 | 20.5 |

(1) Indicative mass per 100 pieces

Description according to UNI EN 10242:

MALE AND FEMALE REDUCTION ELBOW A4 (ex Fig. 92R)

Table 9

## Appendix 6

45° MALE-FEMALE BEND

Material code 33601762.

Figure 1 - Graphical representation

ND	: nominal pipe diameter

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | b mm | z mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- |
| 33601762010 | ¾ | 43 | 36 | 28 | 18.5 |
| 33601762012 | 1 | 51 | 42 | 34 | 29.5 |
| 33601762016 | 1 ½ | 68 | 58 | 49 | 61.2 |
| 33601762020 | 2 | 81 | 70 | 57 | 97.5 |
| 33601762026 | 3 | 113 | 100 | 83 | 211.5 |

(1) Indicative mass per 100 pieces

Description according to UNI EN 10242:

LARGE RADIUS 45° MALE AND FEMALE BEND, G4 / 45°(ex Fig. 40)

Table 18

## Appendix 7

45° FEMALE-FEMALE BEND

Material code 33601762.

Figure 1 - Graphical representation

ND	: nominal pipe diameter

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | z mm | Mass (1) kg |
| --- | --- | --- | --- | --- |
| 33601762040 | ¾ | 43 | 28 | 15.0 |
| 33601762042 | 1 | 51 | 34 | 24.0 |
| 33601762046 | 1 ½ | 68 | 49 | 51.0 |
| 33601762050 | 2 | 81 | 57 | 81.0 |
| 33601762056 | 3 | 113 | 83 | 194.0 |

(1) Indicative mass per 100 pieces

Description according to UNI EN 10242:

LARGE RADIUS 45° BEND G1 / 45°(ex Fig. 41)

Table 18

## Appendix 8

TEE

Material code 336017630.

Figure 1 - Graphical representation

ND	: nominal pipe diameter

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | z mm | Mass (1) kg |
| --- | --- | --- | --- | --- |
| 33601763008 | ½ | 28 | 14 | 15.6 |
| 33601763010 | ¾ | 33 | 18 | 18.7 |
| 33601763012 | 1 | 38 | 21 | 28.2 |
| 33601763016 | 1 ½ | 50 | 31 | 51.0 |
| 33601763020 | 2 | 58 | 34 | 80.0 |
| 33601763026 | 3 | 78 | 48 | 180.0 |

(1) Indicative mass per 100 pieces

Description according to UNI EN 10242:

TEE B1 (ex Fig. 130)

Table 8

## Appendix 9

PITCHER TEE REDUCTION

Material code 336017631.

Figure 1 - Graphical representation

ND	: nominal pipe diameter

Table 1 - Material code and dimensions

| Material code | ND x nd inches | a mm | b mm | z1 mm | z2 mm | Mass (1) kg |
| --- | --- | --- | --- | --- | --- | --- |
| 33601763121 | 1¼ x 1 | 40 | 42 | 21 | 25 | 36.5 |
| 33601763127 | 1½ x 1 | 42 | 46 | 23 | 29 | 43.0 |
| 33601763142 | 2 x 1 | 44 | 52 | 20 | 35 | 60.0 |
| 33601763144 | 2 x 1½ | 52 | 55 | 28 | 36 | 72.0 |
| 33601763172 | 3 x 1 | 51 | 67 | 21 | 50 | 122.0 |
| 33601763174 | 3 x 1½ | 58 | 71 | 28 | 52 | 140.0 |
| 33601763176 | 3 x 2 | 64 | 73 | 34 | 49 | 155.0 |

(1) Indicative mass per 100 pieces

Description according to UNI EN 10242:

PITCHER TEE REDUCTION B1 (ex Fig. 130R)

Table 11

## Appendix 10

CROSS

Material code 336017650.

Figure 1 - Graphical representation

ND	: nominal pipe diameter

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | z mm | Mass (1) kg |
| --- | --- | --- | --- | --- |
| 33601765012 | 1 | 38 | 21 | 37.0 |
| 33601765016 | 1 ½ | 50 | 31 | 63.0 |
| 33601765020 | 2 | 58 | 34 | 100.0 |
| 33601765026 | 3 | 78 | 48 | 200.0 |

(1) Indicative mass per 100 pieces

Description according to UNI EN 10242:

CROSS C1 (ex. Fig. 180)

Table 8

## Appendix 11

MALE-FEMALE REDUCTION, FIG. 241

Material code 336017671.

Model I	Model II	Model III

S

S

S

Figure 1	Figure 2	Figure 3

Graphic representation	Graphic representation	Graphic representation

ND	: nominal pipe diameter

s	: operating spanner

Table 1 - Material code and dimensions

| Material code | ND x ND inches | Model | a mm | b mm | s (1) mm | z mm | Mass (2) kg |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 33601767110 | ¾ x ½ | I | 26 | - | 30 | 13 | 5.2 |
| 33601767115 | 1 x ¾ | I | 29 | - | 36 | 14 | 7.5 |
| 33601767121 | 1¼ x 1 | I | 31 | - | 46 | 14 | 12.5 |
| 33601767126 | 1½ x ¾ | II | 31 | - | 50 | 16 | 23.0 |
| 33601767127 | 1½ x 1 | II | 31 | - | 50 | 14 | 19.0 |
| 33601767128 | 1½ x 1¼ | I | 31 | - | 50 | 12 | 11.0 |
| 33601767142 | 2 x 1 | II | 35 | - | 65 | 18 | 41.0 |
| 33601767143 | 2 x 1¼ | II | 35 | - | 65 | 16 | 34.5 |
| 33601767144 | 2 x 1½ | II | 35 | - | 65 | 16 | 26.5 |
| 33601767165 | 2½ x 2 | II | 40 | - | 80 | 16 | 50.0 |
| 33601767174 | 3 x 1½ | III | 44 | 59 | 95 | 40 | 80.0 |
| 33601767176 | 3 x 2 | II | 44 | - | 95 | 20 | 88.0 |
| 33601767178 | 3 x 2½ | II | 44 | - | 95 | 17 | 56.5 |

(1) Indicative

(2) Indicative mass per 100 pieces

Description according to UNI EN 10242:

REDUCTION N4 (ex Fig. 241)

Table 21

## Appendix 12

MALE-FEMALE SLEEVE, FIG. 246

Material code 336017672.

Figure 1 - Graphical representation

ND	: nominal pipe diameter

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | z mm | Mass (1) kg |
| --- | --- | --- | --- | --- |
| 33601767215 | 1 x ¾ | 55 | 38 | 14.6 |

(1) Indicative mass per 100 pieces

Description according to UNI EN 10242:

MALE AND FEMALE SLEEVE M4 (ex Fig. 246)

Table 20

## Appendix 13

RIGHT THREAD SLEEVE, FIG. 270

Material code 336017673.

Z1

Figure 1 - Graphical representation

ND	: nominal pipe diameter

Table 1 - Material code and dimensions

| Material code | ND inches | c mm | z1 mm | Mass (1) kg |
| --- | --- | --- | --- | --- |
| 33601767310 | ¾ | 39 | 9 | 9.3 |
| 33601767312 | 1 | 45 | 11 | 18.3 |
| 33601767316 | 1½ | 55 | 17 | 24.5 |
| 33601767320 | 2 | 65 | 17 | 40.5 |
| 33601767326 | 3 | 80 | 20 | 93.0 |

(1) Indicative mass per 100 pieces

Description according to UNI EN 10242:

SLEEVE M2 (ex Fig. 270)

Table 19

## Appendix 14

REDUCTION NIPPLE, FIG. 245

Material code 336017674.

S

Figure 1 - Graphical representation

ND	: nominal pipe diameter

s	: operating spanner

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | s (1) mm | Mass (2) kg |
| --- | --- | --- | --- | --- |
| 33601767415 | 1 x ¾ | 53 | 36 | 13.9 |
| 33601767442 | 2 x 1 | 68 | 65 | 41.6 |
| 33601767444 | 2 x 1½ | 68 | 80 | 42.2 |
| 33601767478 | 3 x 2½ | 83 | 95 | 95.4 |

(1) Indicative

(2) Indicative mass per 100 pieces

Description according to UNI EN 10242:

HEXAGONAL REDUCTION NIPPLE N8 (ex Fig. 245)

Table 21

## Appendix 15

NIPPLE

Material code 336017675.

S

Figure 1 - Graphical representation

ND	: nominal pipe diameter

s	: operating spanner

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | s (1) mm | Mass (2) kg |
| --- | --- | --- | --- | --- |
| 33601767510 | ¾ | 47 | 32 | 9.0 |
| 33601767512 | 1 | 53 | 41 | 15.0 |
| 33601767516 | 1½ | 59 | 55 | 26.5 |
| 33601767520 | 2 | 68 | 70 | 40.0 |
| 33601767526 | 3 | 83 | 100 | 85.0 |

(1) Indicative

(2) Indicative mass per 100 pieces

Description according to UNI EN 10242:

HEXAGONAL NIPPLE N8 (ex Fig. 280)

Table 22

## Appendix 16

PLUG

Material code 336017680.

Figure 1 - Graphical representation

ND	: nominal pipe diameter

s	: operating spanner

Table 1 - Material code and dimensions

| Material code | ND inches | c mm | s (1) mm | Mass (2) kg |
| --- | --- | --- | --- | --- |
| 33601768008 | ½ | 26 | 11 | 5.4 |
| 33601768010 | ¾ | 32 | 17 | 7.0 |
| 33601768012 | 1 | 36 | 19 | 9.5 |
| 33601768014 | 1¼ | 39 | 22 | 17.0 |
| 33601768016 | 1½ | 41 | 22 | 21.2 |
| 33601768020 | 2 | 48 | 27 | 34.0 |
| 33601768026 | 3 | 60 | 36 | 81.6 |
| 33601768030 | 4 | 70 | 41 | 110.0 |

(1) Indicative

(2) Indicative mass per 100 pieces

Description according to UNI EN 10242:

PLUG WITH ROUNDED EDGE T9 (ex Fig. 290)

Table 24

## Appendix 17

NUT CAP

Material code 336017681.

S

Figure 1 - Graphical representation

ND	: nominal pipe diameter

s	: operating spanner

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | s (1) mm | Mass (2) kg |
| --- | --- | --- | --- | --- |
| 33601768110 | ¾ | 22 | 32 | 7.5 |
| 33601768116 | 1½ | 27 | 55 | 24.0 |
| 33601768120 | 2 | 32 | 70 | 40.0 |
| 33601768124 | 2½ | 35 | 85 | 63.0 |
| 33601768124 | 3 | 38 | 100 | 93.8 |
| 33601768130 | 4 | 45 | 130 | 155.0 |

(1) Indicative

(2) Indicative mass per 100 pieces

Description according to UNI EN 10242:

FEMALE CAP T1 (ex Fig. 300)

Table 24

## Appendix 18

FLAT-SEAT UNION

Material code 336017683.

G

Figure 1 - Graphical representation

ND	: nominal pipe diameter

s 1	:	operating spanner

s 2	:	operating spanner

G	:	seal

Table 1 - Material code and dimensions

| Material code | ND inches | a mm | s1 (1) mm | s2 (1) mm | z1 mm | Mass (2) kg |
| --- | --- | --- | --- | --- | --- | --- |
| 33601768310 | ¾ | 52 | 32 | 50 | 22 | 28.9 |
| 33601768312 | 1 | 58 | 38 | 55 | 24 | 35.5 |
| 33601768314 | 1¼ | 65 | 48 | 70 | 27 | 62.8 |
| 33601768316 | 1½ | 70 | 54 | 75 | 32 | 74.4 |
| 33601768320 | 2 | 78 | 66 | 90 | 30 | 109.5 |
| 33601768326 | 3 | 95 | 96 | 130 | 36 | 267.1 |

(1) Indicative

(2) Indicative mass per 100 pieces

SEALS: use for transporting methane gas.

It is the responsibility of the supplier to define the material and thickness of the seals (example: NBR elastomer or equivalent high acrylonitrile content; Hardness category 80) in relation to the described use.

Description according to UNI EN 10242:

FLAT-SEAT UNION U1 (formerly Fig. 330)

Table 25

## Appendix 19

MALE-FEMALE FLAT-SEAT UNION

Material code 336017683.

G

Figure 1 - Graphical representation

ND	: nominal pipe diameter

s 1	:	operating spanner

s 2	:	operating spanner

G	:	seal

Table 1 - Material code and dimensions

| Material code | ND inches | b mm | s1 (1) mm | s2 (1) mm | z2 mm | Mass (2) kg |
| --- | --- | --- | --- | --- | --- | --- |
| 33601768372 | 1 | 80 | 38 | 55 | 63 | 44.9 |
| 33601768376 | 1½ | 95 | 54 | 75 | 76 | 94.0 |
| 33601768380 | 2 | 106 | 66 | 90 | 82 | 128.3 |
| 33601768386 | 3 | 130 | 96 | 130 | 100 | 341.0 |

(1) Indicative

(2) Indicative mass per 100 pieces

SEALS: use for transporting methane gas.

It is the responsibility of the supplier to define the material and thickness of the seals (example: Type GAL; NBR elastomer or equivalent high acrylonitrile content; Hardness category 80) in relation to the described use.

Description according to UNI EN 10242:

MALE AND FEMALE FLAT-SEAT UNION, U2 (ex Fig. 331)

Table 25

Appendix 20

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN ISO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

(4)	The following products manufactured by us:

| Our material code (5) | Italgas Reti material code (6) |
| --- | --- |
| xxx | 1761010 |
| xxx | xxx |

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(7)	S.T.V.F.C. 176A300	MALLEABLE CAST IRON FITTINGS, GALVANISED	Edition 1 of xx/xx/2017

Additional information:

(8) 	...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(9) 	.............................................................		...................................................................................................................

(Name and position)				(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- The “subject” must be unambiguously described so that the declaration of conformity can be referred to the subject in question.

- List all the products for which company use authorisation is being requested.

- For each individual product supplied, state the material code used by the Supplier.

- For each individual product supplied, please quote the material code assigned by Italgas Reti, which can be found in the Italgas Reti reference documents. If there are none, please contact SERTEC-NORM.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

Supplier means the party responsible for the design and construction of the products or its legal representative as defined in Legislative Decree no. 206 of 6 September 2005 as amended and supplemented. - "CONSUMER CODE" pursuant to Article 7 of Law no. 229 of 29 July 2003.