“TECHNICAL SPECIFICATION FOR SUPPLY ASSESSMENT AND INSPECTION”

S.T.V.F.C. 1800300

POLYETHYLENE FITTINGS AND SPECIAL PARTS FOR METHANE GAS PIPELINES

| Compiled by | APT-ATECH-NORM | MARELLA MANUELE |
| --- | --- | --- |
|  | APT-ATECH-NORM | NORDIO IVANO |
| Checked by | APT-ATECH-NORM | CIMINO SALVATORE |
| Checked by | PROMA-MATMA | SCOTTO ENRICO |
| Checked by | BDT | AMBROSI LEONARDO |
| Checked by | PROMA/CMMAT | FASSINO SILVIO |
| Checked by | HSEQ | LIMONTA AGOSTINO MASSIMO |
| Approved by | APT-ATECH | GHIBAUDO CLAUDIO |

SUMMARY

1.	PRELIMINARY INFORMATION	3

1.1.	Cancels and replaces	3

1.2.	Reason for issue	3

1.3.	Company departments mentioned in the document	3

2.	PURPOSE AND SCOPE OF APPLICATION	3

2.1.	Purpose	4

2.2.	Field of application	5

3.	SPECIFICATIONS	5

4.	CHARACTERISTICS	5

4.1.	Marking	6

5.	TESTS AND INSPECTIONS	6

5.1.	Polyethylene fittings for electrofusion welding	6

5.2.	Polyethylene fittings for welding by heating elements (head/head)	6

5.3.	Steel/polyethylene transition fittings	7

5.3.1.	 Butt-weld fittings	7

5.3.2.	 Compression fittings	11

5.4.	Polyethylene valves	13

5.5.	Automatic gas flow shut-off devices	15

5.6.	Pipe shut-off device with adapter	16

6.	SUPPLY, PACKAGING AND SHIPPING TERMS	17

6.1.	Polyethylene fittings for electrofusion welding	17

6.2.	 Polyethylene fittings for welding by heating elements (head/head)	18

6.3.	Steel/polyethylene transition fittings	18

6.4.	Compression fittings	18

6.5	Cast iron - PE transition compression fittings	18

6.6         Polyethylene valves	18

6.7            Automatic gas flow shut-off devices	19

7. 	DOCUMENTATION FOR THE APPROVAL FOR COMPANY USE PROCESS	19

8.	REFERENCE STANDARDS	20

9-	Appendices	20

APPENDIX 1	22

APPENDIX 2	32

APPENDIX 3	43

## 1.	PRELIMINARY INFORMATION

### 1.1.	Cancels and replaces

Technical Specification for Supply Assessment and Inspection "Polyethylene fittings and special parts for methane gas pipelines" S.T.V.F.C. 1800300 edition 4 dated 28 February 2019.

### 1.2.	Reason for issue

The update of the Technical Specification 1800300 was required as a result of:

- national regulatory update;

- the introduction of new diameters OD 75-110-140-160-200-250-280 SDR (Standard Dimension Ratio) 11 (S5) and OD 110-140-160-200-250-280 SDR (Standard Dimension Ratio) 17 (S8).

### 1.3.	Company departments mentioned in the document

- PROMA-CMMAT - Category Manager Materials

- APT-ATECH-NORM - Technical Regulations

## 2.	PURPOSE AND SCOPE OF APPLICATION

### 2.1.	Purpose

This Specification applies to polyethylene fittings and special parts normally used for the natural gas distribution network.

Its purpose is to define:

- the characteristics of the material and reference standards;

- the types of checks and type test methods used to obtain authorization for company use.

### 2.2.	Field of application

It applies whenever material covered by this specification must be authorised for company use, produced

by a new potential Supplier or by an existing one.

## 3.	SPECIFICATIONS

These specifications must be understood as an integral part of the "ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS RETI."

## 4.	CHARACTERISTICS

The material characteristics, production, control and certification must meet the reference standards in Chapter 8.

The raw material must have the following additional characteristics:

- it must be PE 100 certified accompanied by a special declaration of compatibility with the PE 50 to PE 80, bi-modal polyethylene pipes currently used by Italgas Reti; the same must also be supplemented by certification issued by accredited Bodies or by documentation of tests carried out by the Supplier, which may be ascertained at Italgas’ request;

- only virgin raw material must be used: the use of previously processed polyethylene, even if regenerated, recycled and/or from the same production, is not permitted;

- appropriate systems must be implemented to ensure that the raw material, at the time of use, has a moisture content less than or equal to that required by the standards mentioned in point 8 and free of any external pollution by water or other foreign bodies; to such purpose, it is recommended that the raw material arrives sealed from origin and is kept sealed until the end of storage; its transfer between storage and the press loading hopper must be carried out directly, guaranteeing sealing and without any possibility of external handling, so as to exclude any chance of pollution.

- the need to subject moulded materials to mechanical processing following injection (e.g. turning) must be limited to particular figures and in any case agreed in advance with Italgas Reti, in order to verify the absence of any possible weakening of the structure.

The drawings shown in the various appendices should be considered as a "standard model shown as an example", except for the specified dimensions and technical characteristics, which should be considered as binding.

### 4.1.	Marking

- The marking of fittings must comply with UNI EN 1555 parts 3 and 4 for "Fittings" and "Valves" respectively.

- As far as the automatic gas shut-off device is concerned, instead, the following must be present:

- indication of the direction of gas flow;

- the word "GAS";

- identification of the manufacturer and/or Supplier;

- diameter and the material;

- operating pressure class (5 bar);

- production date, batch number or serial number.

## 5.	TESTS AND INSPECTIONS

The tests and checks to be carried out by the supplier are those indicated in the reference standards, cited in point 8.

### 5.1.	Polyethylene fittings for electrofusion welding

These must be produced, tested and certified in accordance with the aforementioned standards and the following additional notes:

a)	each individual fitting shall be provided with a bar code, permanently affixed to the body, conforming to type 2.5 interlaced, as referred to in draft standard ISO/TC 138/GT9 no. 127 "DESCRIPTION DU CODE BARRE"; or with a dedicated magnetic card;

b)	only fittings of minimum SDR 11 (S5), of declared weldability on SDR 11 (S5) and SDR 17 (S8) pipes and fittings are accepted;

c)	the fittings must be capable of being welded with a voltage of less than 50 V and must have terminals for electrical connection with a minimum degree of protection IP XXB for protection against direct contacts according to IEC 64-8/7 point 706.4 and IEC EN 60529;

d) for safety reasons, all tee sockets must be fitted with an end stop of the cutter, upwards, in order to avoid incorrect manoeuvres that could allow the obturator to escape – accidentally or thrust by gas pressure – out of its seat, after the drilling and raising of the cutter to activate the utility branch;

e) the cutters inside the tee sockets must be made of material suitable for drilling the most recently manufactured pipes and must be able to hold the "core" of the drill indefinitely;

f)	the figures permitted for company use, with the relevant dimensions, are set out in Appendix 1, which is an integral part of this Specification.

### 5.2.	Polyethylene fittings for welding by heating elements (head/head)

These must be produced, tested and certified in accordance with the aforementioned standards and the following additional notes:

a)	only long spigot fittings are permitted for business use;

b)	the figures permitted for company use, with the relevant dimensions, are set out in Appendix no. 2, which is an integral part of this Specification.

### 5.3.	Steel/polyethylene transition fittings

These must be produced, tested and certified in accordance with the aforementioned standards and the following additional notes.

#### 5.3.1.	 Butt-weld fittings

- Materials:

steel pipe: compliant with the Technical Specification Italgas Reti 15AA300 (steel pipe PSL1 grade "L210 or A" (Rt 0.5 = 210 MPa)

polyethylene pipe: compliant with the Technical Specification Italgas Reti 1627300.

- Ends:

steel: to be butt-welded, with the following finish (where "s" is the thickness of the steel pipe to be coupled:

- flat (UNI ISO 6761), for thicknesses ≤ 3.2 mm;

- externally chamfered with angle α = 30°  37.5° and root face of 1.6 mm ± 0.8 mm, for thicknesses: 3.2 mm < s = s¹ + 1.6 mm;

- tapered internally with angle β  18° (ANSI B 16.25), for thicknesses: 3.2 mm < s > s¹ + 1.6 mm;

|  | - Flat - Chamfered - Tapered |
| --- | --- |

- s = minimum thickness of fitting end

- 	= 30°  37.5°

- 	=  18°

- C	= 1.6  0.8 mm

- s1	= S - C in Figures 2 and 3

- polyethylene: suitable for welding with electrofusion sleeve for all OD and for butt welding for OD  90 mm.

The minimum dimensions required are shown in Tables 1.1 and 1.2.

Table 1.1  Butt weld steel/PE transition fittings SDR 11 (S5)

| Material code | STEEL |  |  |  | POLYETHYLENE |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | ND |  | Thickness mm | Minimum end length (B) mm | ND=OD mm | Thickness (mm) SDR 11 (S5) | Minimum end length (A) mm |
|  | (“) | mm |  |  |  |  |  |
| 33501786212 | 1” | 25 | 2.9 | 300 | 32 | 3 | 100 |
| 33501786218 | 1” ½ | 40 | 2.9 | 300 | 50 | 4.6 | 110 |
| 33501786221 | 2” | 50 | 2.9 | 300 | 63 | 5.8 | 120 |
| 33501786225 | 2” ½ | 65 | 3.2 | 300 | 75 | 6.8 | 130 |
| 33501786227 | 3” | 80 | 3.2 | 300 | 90 | 8.2 | 140 |
| 33501786229 | 4” | 100 | 3.2 | 300 | 110 | 10.0 | 150 |
| 33501786233 | 4” | 100 | 3.2 | 300 | 125 | 11.4 | 160 |
| 33501786235 | 5” | 125 | 3.6 | 300 | 140 | 12.7 | 170 |
| 33501786237 | 5” | 125 | 3.6 | 300 | 160 | 14.6 | 180 |
| 33501786241 | 6” | 150 | 4 | 300 | 180 | 16.4 | 200 |
| 33501786243 | 8” | 200 | 5 | 300 | 200 | 18.2 | 210 |
| 33501786250 | 8” | 200 | 5 | 300 | 225 | 20.5 | 230 |
| 33501786255 | 10” | 250 | 5.6 | 500 | 250 | 22.7 | 250 |
| 33501786257 | 10” | 250 | 5.6 | 500 | 280 | 25.4 | 300 |
| 33501786260 | 12” | 300 | 5.6 | 500 | 315 | 28.7 | 300 |

Table 1.2  Butt weld steel/PE transition fittings SDR 17 (S8)

| Material code | STEEL |  |  |  | POLYETHYLENE |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | ND |  | Thickness mm | Minimum end length (B) mm | ND=OD mm | Thickness (mm) SDR 17 (S8) | Minimum end length (A) mm |
|  | (“) | mm |  |  |  |  |  |
| 33501786427 | 3” | 80 | 3.2 | 300 | 90 | 5.4 | 140 |
| 33501786429 | 4” | 100 | 3.2 | 300 | 110 | 6.6 | 150 |
| 33501786433 | 4” | 100 | 3.2 | 300 | 125 | 7.4 | 160 |
| 33501786435 | 5” | 125 | 3.6 | 300 | 140 | 8.3 | 170 |
| 33501786437 | 5” | 125 | 3.6 | 300 | 160 | 9.5 | 180 |
| 33501786441 | 6” | 150 | 4 | 300 | 180 | 10.7 | 200 |
| 33501786443 | 8” | 200 | 5 | 300 | 200 | 11.9 | 210 |
| 33501786450 | 8” | 200 | 5 | 300 | 225 | 13.4 | 230 |
| 33501786455 | 10” | 250 | 5.6 | 500 | 250 | 14.8 | 250 |
| 33501786457 | 10” | 250 | 5.6 | 500 | 280 | 16.6 | 300 |
| 33501786460 | 12” | 300 | 5.6 | 500 | 315 | 18.7 | 300 |

#### 5.3.2.	 Compression fittings

These must be made with characteristics at least up to those required by UNI 9034 and UNI 9736.

The diameters allowed for company use are: OD 32, 50 and 63.

ND:	nominal diameter

OD:	outer diameter of polyethylene (PE) pipe

NOMINAL PRESSURE: PN 16

MAXIMUM OPERATING PRESSURE: 0.04 bar

ENDS: tapered male thread UNI ISO 7/1, compression fitted, in accordance with DIN 8076/1 and UNI 9736, for polyethylene pipe connection, SDR 11 (S5)

MARKING: nominal diameter marking, manufacturer's acronym

CONSTITUENT ELEMENTS AND MATERIALS:

- brass fitting body

- octagonal brass nut

- metal reinforcement bushing

The required dimensions are shown in Table 2

Metal bushing

Table 2: Compression fittings

| - Material Code | Fitting |  |  |  |  | Bushing |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ND in | OD mm | A min. mm | B: mm | C * mm | D mm | E * mm | F * mm | G * mm | H * mm | ° |
| 33501792805 | 1 | 32 | 19.1 | 60 | 48 | 25.7 | 49 | 28 | 23 | 20 | 1 |
| 33501792809 | 1½ | 50 | 21.4 | 85 | 71 | 40.3 | 57 | 43 | 37 | 22 | 2 |
| 33501792811 | 2 | 63 | 25.7 | 102 | 88.5 | 50.9 | 70 | 52.5 | 45 | 27 | 2 |

* Approximate dimensions

5.3.3.	 Cast iron - PE transition compression fittings

These must be made with characteristics at least up to those required by UNI 9034 and UNI 9736.

ND: nominal pipe diameter

OD: outer diameter of the polyethylene end

CONSTITUENT ELEMENTS AND MATERIALS:

- spheroidal cast iron or steel body

- NBR elastomer seal compliant with UNI EN 682 or equivalent

- bolt complete with washer

- spheroidal cast iron or steel mobile compression flange

- polyethylene pipe compliant with the Technical Specification Italgas Reti 1627300 SDR 17 (S8)

NOMINAL PRESSURE: 16 bar

MAXIMUM OPERATING PRESSURE: 0.5 bar

TIGHTENING TORQUE: indicated on the plate attached to the joint body or on the accompanying instruction sheet

END (PE side) smooth: suitable for welding with electrofusion sleeve for all ODs and for butt welding for OD  90 mm.

MARKINGS: supplier's name or trademark, range of applicability of the joint

CONSTRUCTION: compliant with UNI 9034

CORROSION PROTECTION:

- body and flanges coated with corrosion protection such as RILSAN NYLON 11 or others suitable for the purpose;

- screws, nuts and washers, if not in stainless steel, coated with corrosion protection such as RILSAN NYLON 11 or others suitable for the purpose.

- The required dimensions are shown in Table 3.

- Table 3 Cast iron - PE transition compression fittings

| - Material code | - Cast iron pipe |  | - Application - on pipes | - Polyethylene pipe |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | - ND - pipes - (mm) | - OD pipes - (min ÷ max) - (mm) |  | - OD - (mm) | - s - (mm) | - A - minimum - (mm) |
| 33501786460 | - 80 | - 93.4 ÷ 102.6 | - GG - GS | - 90 | - 5.4 | - 160 |
| 33501786463 | - 100 | - 113.4 ÷ 122.7 | - GG - GS | - 125 | - 7.4 | - 200 |
| 33501786467 | - 125 | - 139.3 ÷ 148.7 | - GG - GS | - 125 | - 7.4 | - 200 |
| 33501786470 | - 150 | - 164.5 ÷ 175.5 | - GG - GS | - 180 | - 10.7 | - 260 |
| 33501786473 | - 200 | - 216.5 ÷ 227.5 | - GG - GS | - 225 | - 13.4 | - 300 |
| 33501786477 | - 250 | - 270 ÷ 289.5 | - GG - GS | - 315 | - 18.7 | - 300 |
| 33501786480 | - 300 | - 322 ÷ 336 | - GG - GS | - 315 | - 18.7 | - 300 |

- GG	:	Grey cast iron pipes

- GS	:	Spheroidal cast iron pipes

- OD (min ÷ max): range of outer pipe diameters for which optimal use

- of the transition fitting is possible.

### 5.4.	Polyethylene valves

- These must be produced, checked and certified in compliance with the provisions of:

- UNI EN 1555 part 4;

as well as the following supplementary requirements:

- valves must be "CE" marked in accordance with Directive 2014/68/EU;

- valves must be able to be used without risk in explosive atmospheres and therefore, in relation to the provisions of Legislative Decree no. 233 of 12 June 2003, (implementation of Directive 1999/92/EC on minimum requirements for improving the safety and health protection of workers exposed to the risk of explosive atmospheres), must comply with the relevant provisions of Legislative Decree no. 85 of 19 May 2016 - "Implementation of Directive 2014/34/EU on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres", where applicable.

Specifically, compliance with this requirement must be demonstrated, if the product falls within the scope of Legislative Decree no. 85/2016, by the product "marking" and by the issue of all the documentation required, as appropriate, by the aforementioned Decree and by the relevant harmonised standards (e.g. EC declaration of conformity or certificate of conformity, operating and maintenance instructions in Italian, any certificate of conformity following EC type-test).

In other cases, the manufacturer must issue a declaration stating, under its own responsibility, that following the ATEX analysis carried out, the product does not present any potential ignition sources, and therefore does not fall within the scope of Legislative Decree no. 85/2016 and can therefore be installed in all types of zones as set out in Legislative Decree no. 233/03.

It should be noted that all valves must be installed in Zone 2 according to Legislative Decree no. 233 of 12 June 2003 (admitted equipment category 3G or higher);

- the raw material used must already be suitably stabilised according to the requirement of the standards in force as per point 4 and classified as PE 100 (MRS 10) for the production of branded valves complying with the draft standard UNI EN 1555/4; the reuse of non-virgin polyethylene, even if regenerated, recycled and/or belonging to the same production, is forbidden;

- only raw materials classified PE 100 may be used, in which case a special declaration of compatibility with PE materials (from PE 50 to bimodal PE 80) used by the Italgas Group must be provided; the same must also be supplemented by certification issued by accredited bodies or by documentation of tests carried out by the Supplier, which can be ascertained on our request;

- valve ends are SDR 11 (S5), and must be suitable for welding with electrofusion sleeve for all ODs and for butt welding for OD  90 mm.

- valves must have flat ends perpendicular to the axis and must be fitted with a support plate for positioning on the ground, where they are directly buried with control relayed to the manhole, depending on the valve model, by means of:

  - extension rod fitted with an anti-unthreading device at one end to be connected onto the valve square and with the square head at the other end, made of material suitable to withstand corrosion and torsion, which guarantees functioning of the valve opening and closing operations; the rod is protected by a PVC pipe complete with closing cap;

  - extension rod with connection of the square head directly to the manhole;

- the valves must be equipped with a system that clearly indicates the position of the ball, e.g. by means of a notch made on the square head and the indication of the opening and closing direction in accordance with the requirements of UNI EN 1555/4;

- the joint is generally made by means of electrofusion sleeves, but butt welding must also be possible;

- in the case of valves made by assembling two pieces of pipe - butt-welded in the factory - to the body, these must comply with the Technical Specification Italgas Reti 1627300.

The required dimensions are shown in Table 4.

Table 4: Polyethylene valves

| Code Material | OD mm | s mm | A max mm | B mm | h mm | H mm |
| --- | --- | --- | --- | --- | --- | --- |
| 40102071904 | 32 | 3 | 110 | 22 x 22 | 700 | 950 |
| 40102071907 | 50 | 4.6 |  |  |  |  |
| 40102071910 | 63 | 5.8 |  |  |  |  |
| 40102071912 | 75 | 6.8 |  |  |  |  |
| 40102071914 | 90 | 8.2 |  |  |  |  |
| 40102071915 | 110 | 10.0 |  |  |  |  |
| 40102071917 | 125 | 11.4 |  |  |  |  |
| 40102071919 | 140 | 12.7 |  |  |  |  |
| 40102071921 | 160 | 14.6 |  |  |  |  |
| 40102071924 | 180 | 16.4 |  |  |  |  |
| 40102071925 | 200 | 18.2 |  |  |  |  |
| 40102071927 | 225 | 20.5 |  |  |  |  |
| 40102071928 | 250 | 22.7 |  |  |  |  |
| 40102071929 | 280 | 25.4 |  |  |  |  |
| 40102071930 | 315 | 28.7 |  |  |  |  |

1= extension rod (h = 500 mm) fitted with an anti-unthreading device to be coupled to the valve-body square head. The indicated length can be changed according to operating requirements

2= extension rod with connection of the square head directly in the manhole.

### 5.5.	Automatic gas flow shut-off devices

These may be supplied as follows provided they have been approved in advance by the responsible Department of Italgas Reti, APT-ATECH-NORM:

- inserted into the appropriate adapter, for use on polyethylene pipes (see point 5.6);

- inserted into the branch end of the polyethylene pressure socket tee (see Appendix 1, point 2).

They must have the following technical characteristics:

- operating pressure: 0.1 to 0.5 MPa (1 5 bar); SDR 11 (S5);

- operating temperature: -20°C to +45°C;

- nature of the gas: natural gas, propane and derivatives;

- mounting position: horizontal, but also operating at an angle of 45°;

- minimum required flow rate of socket + trigger device at 0.1 MPa (1 bar): 25 m³/h for the OD 20 mm pipe and 100 m³/h for the OD 32 mm pipe;

- closing response time: less than 1 second;

- permissible leakage: less than 0.15 dm3 with natural gas (0.11 dm3 with air);

- resistant to gas components;

- resettable by balancing upstream pressure with downstream pressure;

- in the case of point b), the Supplier must guarantee dimensional compatibility between the device and the tee socket in which it is inserted: no leakage is permitted between the internal surface of the branch (housing seat of the device) and the device itself.

- The cut-in values are given in Table 5.

- Table 5: Cut-in values

| - Outer diameter of PE pipe | - Nominal device capacity | - Minimum cut-in value | - Maximum cut-in value at - 0.1 MPa | - Maximum cut-in value - at - 0.5 MPa |
| --- | --- | --- | --- | --- |
| - 20 mm | - 25 m³/h | - 40 m³/h | - 50 m³/h | - 90 m³/h |
| - 32 mm | - 100 m³/h | - 160 m³/h | - 200 m³/h | - 360 m³/h |

### 5.6.	Pipe shut-off device with adapter

- OD	: outer diameter

- ID: internal diameter

- s: thickness, corresponding to SDR11 (S5)

- L: adapter length

1. polyethylene adapter (PE 100), SDR11 (S5)

2. polyphenylene sulphide (PPS) device body

3. nitrile butadiene rubber (NBR) seals

4. austenitic stainless steel spring (X2 NiCrMoCu 25205 - 1.4539)

5. end caps

- The required dimensions are shown in Table 6.

- Table 6: Automatic shut-off device

| - Material code | - OD - mm | - Min. length (L) - mm | - Thickness (s) - mm |
| --- | --- | --- | --- |
| 40102071983 | - 32 | - 120 | - 3 |

## 6.	SUPPLY, PACKAGING AND SHIPPING TERMS

The Supplier shall ensure compliance with the requirements set out in this Technical Specification and the applicable regulations by means of a suitable control and inspection system, with particular attention to the marking of individual fittings.

The packaging, produced in compliance with the regulations in force, must prevent exposure to UV rays, damage to the material contained therein during transport and handling and allow, by means of labelling, the identification of the products and the quantity, without having to open the packages to check the content.

Furthermore, both on the packaging and on the delivery notes the material must be identified with the Client code, contained in this Technical Specification.

Specific indications for each type of material are given below.

### 6.1.	Polyethylene fittings for electrofusion welding

The material must be individually packaged in a sealed transparent or opaque plastic bag. If the plastic bag prevents the required markings (e.g. date of manufacture) from being seen, a label with such markings must be affixed to it. UV protection is ensured by subsequent packaging in a cardboard box containing a quantity of the same articles.

### 6.2.	 Polyethylene fittings for welding by heating elements (head/head)

As in point 6.1.

### 6.3.	Steel/polyethylene transition fittings

The name of the manufacturer, the date of manufacture, the ND of the steel pipe and the OD of the PE pipe must be indicated on the material. Packaging as in point 6.1.

### 6.4.	Compression fittings

The material can be packaged not individually in cardboard boxes. The box must be labelled as indicated in point 6.

### 6.5	Cast iron - PE transition compression fittings

The name of the manufacturer, the date of manufacture, the ND of the cast iron pipe and the OD of the PE pipe must be indicated on the material. Packaging as in point 6.1.

### 6.6         Polyethylene valves

Valves must be supplied individually packaged in cardboard boxes to ensure protection from UV rays and impact.

The individual packaging must also contain all the accessories (extension rods) required for its correct use.

The required valve markings should also be indicated on the packaging by means of a label.

### 6.7            Automatic gas flow shut-off devices

These must be individually packaged in a sealed transparent or opaque plastic bag. If the plastic bag prevents the required markings (e.g. date of manufacture) from being seen, a label with such markings must be affixed.

Assembly instructions and adhesive labels, with indelible writing indicating the type of device and the pressure range of use, should be placed inside each package:

- one on the adapter body or on the tee socket;

- one to be placed inside the measuring unit housing, to indicate the presence of the device.

## 7. 	DOCUMENTATION FOR THE APPROVAL FOR COMPANY USE PROCESS

The prospective Supplier must submit the following documentation to the PROMA-CMMAT Department at the tender stage:

- “Declaration of conformity” with this technical specification and any specific documents mentioned in it (legal provisions, applied standards, MID Directive, ATEX, EMC, PED, etc.) to which the supplier refers for the design and construction of the product, as indicated in the UNI CEI EN ISO/IEC 17050-1 standard (see the example given in APPENDIX 1 of this technical specification).

Italgas Reti, through its Department APT-ATECH-NORM, reserves the right to request the Supplier:

- to produce further technical documentation and/or drawings;

- to carry out any laboratory and/or field tests to check the conformity of the proposed products with the content of this Appendix and the standards it refers to.

- Any other technical documents and/or drawings requested by the relevant Italgas Reti departments,

- “Operating Instructions” for the correct use of the product;

- "Certificate of conformity", issued by a recognised certification body, to Legislative Decree no. 26 of 15 February 2016 as amended (PED Directive).

- If, on the basis of the design of a project intended for use under pressure (PED Directive), the Supplier determines that its product does not have the characteristics defined by the aforementioned directive, it must in any case submit a declaration of inclusion within art. 3 paragraph 3 of the aforementioned directive to certify the exemption of the product in compliance with the provisions of the same paragraph;

- a FAC-SIMILE of the marking on the product, or on the accompanying documents, bearing the data required by Legislative Decree 85 of 16 May 2016 (where applicable), Legislative Decree no. 26 of 15 February 2016, as amended, and by the technical standards applied.

## 8.	REFERENCE STANDARDS

- Ministerial Decree of 16 April 2008 - “Technical regulations for the design, construction, testing, operation and supervision of works and distribution systems and direct lines for natural gas with a density not exceeding 0.8”.

- UNI EN 1555 - “Plastic piping systems for the supply of gaseous fuels”.

- Part 1 – General.

- Part 2 – Pipes.

- PART 3 – Fittings

- PART 4 – Valves

- PART 5 – “Fitness for purpose of the system”;

- PART 7 – “Guidance for the assessment of conformity”.

- UNI 9034 - "Gas distribution pipelines with maximum operating pressures  5 bar";

- UNI 9736 - "Pipe joints and fittings in combination and mixed metal- polyethylene-joints for buried pipelines";

- UNI EN 682 - "Elastomeric seals – requisites of elastomeric materials used in pipes and fittings carrying gas and hydrocarbon fluids";

- UNI EN ISO 3183 “Petroleum and natural gas industries - Steel pipe for pipeline transportation systems”

- UNI CEI EN ISO/IEC 45014 - "General criteria for a supplier’s declaration of conformity”;

- UNI EN ISO 9000-9001-9004:2000 "Vision 2000 Package. Quality management systems – foundations and terminology – requirements – guidelines for improving  performance";

- Legislative Decree no. 85 of 19 May 2016 - "Implementation of Directive 2014/34/EU on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres". (ATEX 1)

- Legislative Decree no. 233 of 12 June 2003 - "Implementation of Directive 1999/92/EC on minimum requirements for improving the safety and health protection of workers exposed to the risk of explosive atmospheres". (ATEX 2)

- Legislative Decree no. 26 of 15 February 2016 - "Implementation of Directive 2014/68/EC of the European Parliament and Council dated 15 May 2014 on the harmonisation of the laws of the Member States relating to making pressure equipment available on the market (recast)".

## 9-	Appendices

Appendix 1:	SDR 11 (S5) polyethylene fittings for electrofusion

Figures and dimensions allowed for company use

Appendix 2:	Polyethylene fittings for butt-welding

Figures and dimensions allowed for company use

Appendix 3:	Sample Declaration of Conformity

##### APPENDIX 1

SDR 11 (S5) polyethylene fittings for electrofusion

Figures and dimensions allowed for company use

- Tee socket

| Code | OD x od | Min d | s | Min L | Code | OD x od | Min d | s | Min L |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| material | mm | mm | mm | mm | material | mm | mm | mm | mm |
| 33501881010 | 50 x 20 | 15 | 3 | 41 | 33501881042 | 140 x 32 | 25 | 3 | 44 |
| 33501881012 | 50 x 32 | 15 | 3 | 44 | 33501881043 | 140 x 40* | 30 | 3 | 49 |
| 33501881016 | 63 x 20 | 15 | 3 | 41 | 33501881044 | 140 x 50 | 28 | 4.6 | 55 |
| 33501881018 | 63 x 32 | 20 | 3 | 44 | 33501881045 | 140 x 63 | 28 | 5.8 | 63 |
| 33501881020 | 63 x 50 | 28 | 4.6 | 55 | 33501881048 | 160 x 50 | 28 | 4.6 | 55 |
| 33501881021 | 75 x 20 | 15 | 3 | 41 | 33501881049 | 160 x 63 | 28 | 5.8 | 63 |
| 33501881022 | 75 x 32 | 15 | 3 | 44 | 33501881058 | 180 x 20 | 15 | 3 | 41 |
| 33501881024 | 75 x 50 | 28 | 4.6 | 55 | 33501881080 | 180 x 32 | 25 | 3 | 44 |
| 33501881026 | 75 x 63 | 28 | 5.8 | 63 | 33501881079 | 180 x 50 | 28 | 4.6 | 55 |
| 33501881023 | 90 x 20 | 15 | 3 | 41 | 33501881082 | 180 x 63 | 28 | 5.8 | 63 |
| 33501881025 | 90 x 32 | 15 | 3 | 44 | 33501881083 | 200 x 32 | 25 | 3 | 44 |
| 33501881027 | 90 x 50 | 28 | 4.6 | 55 | 33501881084 | 200 x 63 | 28 | 5.8 | 63 |
| 33501881028 | 90 x 63 | 28 | 5.8 | 63 | 33501881067 | 225 x 20 | 15 | 3 | 41 |
| 33501881029 | 110 x 32 | 25 | 3 | 44 | 33501881069 | 225 x 32 | 25 | 3 | 44 |
| 33501881031 | 110 x 40* | 25 | 3 | 49 | 33501881071 | 225 x 50 | 28 | 4.6 | 55 |
| 33501881032 | 110 x 50 | 28 | 4.6 | 55 | 33501881072 | 225 x 63 | 28 | 5.8 | 63 |
| 33501881033 | 110 x 63 | 28 | 5.8 | 63 | 33501881073 | 250 x 32 | 25 | 3 | 44 |
| 33501881038 | 125 x 20 | 15 | 3 | 41 | 33501881074 | 250 x 63 | 28 | 5.8 | 63 |
| 33501881040 | 125 x 32 | 25 | 3 | 44 | 33501881085 | 315 x 32 | 25 | 3 | 44 |
| 33501881044 | 125 x 50 | 28 | 4.6 | 55 | 33501881087 | 315 x 50 | 28 | 4.6 | 55 |
| 33501881041 | 125 x 63 | 28 | 5.8 | 63 | 33501881088 | 315 x 63 | 28 | 5.8 | 63 |

L = length of the branch in accordance with UNI EN 1555/3

d = minimum diameter of the intake hole on the PE road pipe

*= diameter normally not used by Italgas Reti

2. 	Tee socket with automatic shut-off device

| Code material | OD x od mm | Min d mm | Min L mm |
| --- | --- | --- | --- |
| 33501880111 | 50 x 20 | 15 | 44 |
| 33501880113 | 50 x 32 | 15 | 65 |
| 33501880121 | 63 x 20 | 15 | 44 |
| 33501880123 | 63 x 32 | 20 | 65 |
| 33501880125 | 75 X 20 | 15 | 44 |
| 33501880126 | 75 X 32 | 25 | 65 |
| 33501880131 | 90 x 20 | 15 | 44 |
| 33501880133 | 90 x 32 | 25 | 65 |
| 33501880134 | 110 x 32 | 25 | 65 |
| 33501880151 | 125 x 20 | 15 | 44 |
| 33501880153 | 125 x 32 | 25 | 65 |
| 33501880155 | 140 x 20 | 15 | 44 |
| 33501880156 | 140 x 32 | 25 | 65 |
| 33501880161 | 160 x 20 | 15 | 44 |
| 33501880163 | 160 x 32 | 25 | 65 |
| 33501880171 | 180 x 20 | 15 | 44 |
| 33501880173 | 180 x 32 | 25 | 65 |
| 33501880175 | 200 x 20 | 15 | 44 |
| 33501880176 | 200 x 32 | 25 | 65 |
| 33501880181 | 225 x 20 | 15 | 44 |
| 33501880183 | 225 x 32 | 25 | 65 |
| 33501880185 | 250 x 20 | 15 | 44 |
| 33501880186 | 250 x 32 | 25 | 65 |
| 33501880188 | 280 x 20 | 15 | 44 |
| 33501880189 | 280 x 32 | 25 | 65 |
| 33501880191 | 315 x 20 | 15 | 44 |
| 33501880193 | 315 x 32 | 25 | 65 |

L min = minimum length of the branch in accordance with UNI EN 1555/3

d min = minimum diameter of the intake hole

s = thickness of the branch: 3 mm

3. 	Sleeve

| Material code | ID mm | Max L mm | Min Ls mm |
| --- | --- | --- | --- |
| 27601887007 | 20 | 41 | 10 |
| 27601887012 | 32 | 44 | 10 |
| 27601887018 | 50 | 55 | 10 |
| 27601887021 | 63 | 63 | 11 |
| 27601887024 | 75 | 70 | 12 |
| 27601887027 | 90 | 79 | 13 |
| 27601887031 | 110 | 82 | 15 |
| 27601887033 | 125 | 87 | 16 |
| 27601887035 | 140 | 92nd | 18 |
| 27601887039 | 160 | 98 | 20 |
| 27601887042 | 180 | 105 | 21 |
| 27601887045 | 200 | 112 | 23 |
| 27601887048 | 225 | 120 | 26 |
| 27601887050 | 250 | 122 | 33 |
| 27601887053 | 280 | 125 | 35 |
| 27601887057 | 315 | 150 | 39 |

L max = maximum shrink-fit length in accordance with UNI EN 1555/3

Ls min = minimum length of the electrofusion zone according to UNI EN 1555/3

4. 	Sleeve for shut-off balloons

| Material code | OD mm | d mm |
| --- | --- | --- |
| 27601885027 | 90 | > 50 |
| 27601885030 | 110 | > 50 |
| 27601885033 | 125 | > 50 |
| 27601885035 | 140 | > 57 |
| 27601885039 | 160 | > 57 |
| 27601885042 | 180 | > 57 |
| 27601885045 | 200 | > 57 |
| 27601885048 | 225 | > 57 |
| 27601885050 | 250 | > 57 |
| 27601885055 | 280 | > 57 |
| 27601885057 | 315 | > 57 |

the dimensions of the fitting must comply with UNI EN 1555/3

d = minimum hole diameter

5. 	Branch sleeves

| Material code | OD x od mm | Min d mm | s mm | Max L mm |
| --- | --- | --- | --- | --- |
| 33501883021 | 63 x 50 | 25 | 4.6 | 55 |
| 33501883025 | 75 X 50 | 40 | 4.6 | 55 |
| 33501883028 | 90 x 50 | 40 | 4.6 | 55 |
| 33501883030 | 110 x 50 | 40 | 4.6 | 55 |
| 33501883034 | 125 x 50 | 40 | 4.6 | 55 |
| 33501883035 | 140 x 50 | 40 | 4.6 | 55 |
| 33501883040 | 160 x 50 | 40 | 4.6 | 55 |
| 33501883043 | 180 x 50 | 40 | 4.6 | 55 |
| 33501883045 | 200 x 50 | 40 | 4.6 | 55 |
| 33501883046 | 200 x 63 | 50 | 5.8 | 63 |
| 33501883049 | 225 x 50 | 40 | 4.6 | 63 |
| 33501883050 | 225 x 63 | 50 | 5.8 | 63 |
| 33501883055 | 250 x 50 | 40 | 4.6 | 63 |
| 33501883056 | 250 x 63 | 50 | 5.8 | 63 |
| 33501883057 | 280 x 50 | 40 | 4.6 | 63 |
| 33501883058 | 280 x 63 | 50 | 5.8 | 63 |
| 33501883060 | 315 x 50 | 40 | 4.6 | 63 |
| 33501883061 | 315 x 63 | 50 | 5.8 | 63 |

the dimensions of the fitting must comply with UNI EN 1555/3

d min = minimum hole diameter

L = maximum turret height

od = outer diameter of the turret

OD = inner diameter of the sleeve

6. 	45° bends for electrofusion

| Material code | OD mm | Max L mm |
| --- | --- | --- |
| 27601884110 | 20 | 41 |
| 27601884116 | 32 | 44 |
| 27601884120 | 50 | 55 |
| 27601884124 | 63 | 63 |
| 27601884125 | 75 | 70 |
| 27601884126 | 90 | 79 |
| 27601884128 | 110 | 82 |
| 27601884130 | 125 | 87 |
| 27601884132 | 140 | 92nd |
| 27601884134 | 160 | 98 |
| 27601884136 | 180 | 105 |
| 27601884138 | 200 | 112 |
| 27601884140 | 225 | 120 |
| 27601884151 | 250 | 129 |
| 27601884153 | 280 | 139 |
| 27601884141 | 315 | 150 |

L = shrink-fit length in accordance with UNI EN 1555/3

7. 	90° bends for electrofusion

| Code material | OD mm | Max L mm |
| --- | --- | --- |
| 27601884010 | 20 | 41 |
| 27601884016 | 32 | 44 |
| 27601884020 | 50 | 55 |
| 27601884024 | 63 | 63 |
| 27601884025 | 75 | 70 |
| 27601884026 | 90 | 79 |
| 27601884028 | 110 | 82 |
| 27601884030 | 125 | 87 |
| 27601884032 | 140 | 92nd |
| 27601884034 | 160 | 98 |
| 27601884036 | 180 | 105 |
| 27601884038 | 200 | 112 |
| 27601884040 | 225 | 120 |
| 27601884051 | 250 | 129 |
| 27601884053 | 280 | 139 |
| 27601884041 | 315 | 150 |

L = shrink-fit length in accordance with UNI EN 1555/3

8. 	90° Tee for electrofusion

| Material code | OD mm | Max L mm |
| --- | --- | --- |
| 27601884210 | 20 | 41 |
| 27601884216 | 32 | 44 |
| 27601884220 | 50 | 55 |
| 27601884224 | 63 | 63 |
| 27601884225 | 75 | 70 |
| 27601884226 | 90 | 79 |
| 27601884228 | 110 | 82 |
| 27601884230 | 125 | 87 |
| 27601884232 | 140 | 92nd |
| 27601884234 | 160 | 98 |
| 27601884236 | 180 | 105 |
| 27601884238 | 200 | 112 |
| 27601884240 | 225 | 120 |
| 27601884251 | 250 | 129 |
| 27601884253 | 280 | 139 |
| 27601884241 | 315 | 150 |

L = shrink-fit length in accordance with UNI EN 1555/3

N.B. The 90° Tee with three ends for electrofusion is also permissible for company use.

9. 	Reducer for electrofusion

| Material code | OD x od mm | L x L1 mm |
| --- | --- | --- |
| 27601884310 | 50x20 | 55x41 |
| 27601884316 | 50x32 | 55x44 |
| 27601884320 | 63x20 | 63x40 |
| 27601884324 | 63x32 | 63x44 |
| 27601884326 | 63x50 | 63x55 |
| 27601884328 | 75x63 | 70x63 |
| 27601884330 | 90x50 | 79x55 |
| 27601884336 | 90x63 | 79x63 |
| 27601884337 | 90x75 | 79x70 |
| 27601884338 | 110x90 | 82x79 |
| 27601884340 | 125x90 | 87x79 |
| 27601884341 | 125x110 | 87x82 |
| 27601884343 | 140x125 | 92x87 |
| 27601884345 | 140x90 | 92x79 |
| 27601884347 | 160x125 | 98x87 |
| 27601884350 | 180x125 | 105x87 |
| 27601884355 | 200x160 | 112x98 |
| 27601884356 | 200x180 | 112x105 |
| 27601884357 | 250x180 | 129x105 |
| 27601884358 | 280x200 | 139x112 |
| 27601884360 | 315x200 | 150x112 |

L x L1= shrink-fit length in accordance with UNI EN 1555/3

10. 	Butt-end caps for electrofusion

| Material code | OD mm | Max L mm |
| --- | --- | --- |
| 27601884410 | 20 | 41 |
| 27601884416 | 32 | 44 |
| 27601884420 | 50 | 55 |
| 27601884424 | 63 | 63 |
| 27601884428 | 75 | 70 |

L = shrink-fit length in accordance with UNI EN 1555/3

##### APPENDIX 2

SDR 17 (S8) and SDR 11 (S5) butt-weld polyethylene fittings

Figures and dimensions allowed for company use

- 45° BENDS

1.1. 	45° Bend SDR 17 (S8)

| Material Code | OD mm | Thickness mm | Min L mm |
| --- | --- | --- | --- |
| 27601855027 | 90 | 5.4 | 83 |
| 27601855028 | 110 | 6.6 | 93 |
| 27601855033 | 125 | 7.4 | 93 |
| 27601855035 | 140 | 8.3 | 97 |
| 27601855037 | 160 | 9.5 | 108 |
| 27601855042 | 180 | 10.7 | 108 |
| 27601855045 | 200 | 11.9 | 118 |
| 27601855048 | 225 | 13.4 | 120 |
| 27601855051 | 250 | 14.8 | 134 |
| 27601855053 | 280 | 16.6 | 145 |
| 27601855049 | 315 | 18.7 | 154 |

1.2.	45° Bend SDR 11 (S5)

| Material code | OD mm | Thickness mm | Min L mm |
| --- | --- | --- | --- |
| 27601853027 | 90 | 8.2 | 83 |
| 27601853028 | 110 | 10.0 | 93 |
| 27601853033 | 125 | 11.4 | 93 |
| 27601853035 | 140 | 12.7 | 97 |
| 27601853037 | 160 | 14.6 | 108 |
| 27601853042 | 180 | 16.4 | 108 |
| 27601853045 | 200 | 18.2 | 118 |
| 27601853048 | 225 | 20.5 | 120 |
| 27601853051 | 250 | 22.7 | 134 |
| 27601853053 | 280 | 25.4 | 145 |
| 27601853049 | 315 | 28.7 | 154 |

L = shrink-fit length in accordance with UNI EN 1555/3

2. 	90° BEND

2.1	90° bend SDR 17 (S8)

| Material code | OD mm | Thickness mm | Min L mm |
| --- | --- | --- | --- |
| 27601854027 | 90 | 5.4 | 83 |
| 27601854028 | 110 | 6.6 | 93 |
| 27601854033 | 125 | 7.4 | 93 |
| 27601854035 | 140 | 8.3 | 97 |
| 27601854037 | 160 | 9.5 | 108 |
| 27601854042 | 180 | 10.7 | 108 |
| 27601854045 | 200 | 11.9 | 118 |
| 27601854048 | 225 | 13.4 | 120 |
| 27601854051 | 250 | 14.8 | 134 |
| 27601854053 | 280 | 16.6 | 145 |
| 27601854049 | 315 | 18.7 | 154 |

2.2.	90° Bend SDR 11 (S5)

| Material code | OD mm | Thickness mm | Min L mm |
| --- | --- | --- | --- |
| 27601851027 | 90 | 8.2 | 83 |
| 27601851028 | 110 | 10.0 | 93 |
| 27601851033 | 125 | 11.4 | 93 |
| 27601851035 | 140 | 12.7 | 97 |
| 27601851037 | 160 | 14.6 | 108 |
| 27601851042 | 180 | 16.4 | 108 |
| 27601851045 | 200 | 18.2 | 118 |
| 27601851048 | 225 | 20.5 | 120 |
| 27601851051 | 250 | 22.7 | 134 |
| 27601851053 | 280 | 25.4 | 145 |
| 27601851049 | 315 | 28.7 | 154 |

L = shrink-fit length in accordance with UNI EN 1555/3

3. 	90° TEE

3.1. 	90° TEE SDR 17 (S8)

| Material code | OD mm | Thickness mm | Min L mm |
| --- | --- | --- | --- |
| 27601864027 | 90 | 5.4 | 83 |
| 27601864028 | 110 | 6.6 | 93 |
| 27601864033 | 125 | 7.4 | 93 |
| 27601864035 | 140 | 8.3 | 97 |
| 27601864037 | 160 | 9.5 | 108 |
| 27601864042 | 180 | 10.7 | 108 |
| 27601864045 | 200 | 11.9 | 118 |
| 27601864048 | 225 | 13.4 | 120 |
| 27601864051 | 250 | 14.8 | 134 |
| 27601864053 | 280 | 16.6 | 145 |
| 27601864049 | 315 | 18.7 | 154 |

3.2 	90° TEE SDR 11 (S5)

| Material code | OD mm | Thickness mm | Min L mm |
| --- | --- | --- | --- |
| 27601861027 | 90 | 8.2 | 83 |
| 27601861028 | 110 | 10.0 | 93 |
| 27601861033 | 125 | 11.4 | 93 |
| 27601861035 | 140 | 12.7 | 97 |
| 27601861037 | 160 | 14.6 | 108 |
| 27601861042 | 180 | 16.4 | 108 |
| 27601861045 | 200 | 18.2 | 118 |
| 27601861048 | 225 | 20.5 | 120 |
| 27601861051 | 250 | 22.7 | 134 |
| 27601861053 | 280 | 25.4 | 145 |
| 27601861049 | 315 | 28.7 | 154 |

L = shrink-fit length in accordance with UNI EN 1555/3

4. 	90° REDUCED TEE

4.1. 	90° reduced tee SDR 17 (S8)

| Material code | OD x od mm | Thickness mm | L x L1 mm |
| --- | --- | --- | --- |
| 27601865042 | 125x90 | 7.4x5.4 | 87x79 |
| 27601865043 | 125x110 | 7.4x6.6 | 87x82 |
| 27601865047 | 140x90 | 8.3x5.4 | 92x79 |
| 27601865048 | 160x125 | 9.5x7.4 | 98x87 |
| 27601865058 | 180x90 | 10.7x5.4 | 105x79 |
| 27601865060 | 180x125 | 10.7x7.4 | 105x87 |
| 27601865062 | 200x90 | 11.9x5.4 | 112x79 |
| 27601865064 | 200x160 | 11.9x9.5 | 112x98 |
| 27601865073 | 225x90 | 13.4x5.4 | 120x79 |
| 27601865074 | 225x125 | 13.4x7.4 | 120x87 |
| 27601865076 | 225x180 | 13.4x10.7 | 120x105 |
| 27601865077 | 250x110 | 14.8x6.6 | 129x82 |
| 27601865078 | 250x125 | 14.8x7.1 | 129x87 |
| 27601865079 | 280x110 | 16.6x6.6 | 139x82 |
| 27601865080 | 315x125 | 18.7x7.4 | 150x87 |
| 27601865081 | 315x225 | 18.7x13.4 | 150x120 |

4.2. 	90° reduced tee SDR 11 (S5)

| Material code | OD x od mm | Thickness mm | L x L1 mm |
| --- | --- | --- | --- |
| 27601863026 | 90x50 | 8.2x4.6 | 79x55 |
| 27601863028 | 90x63 | 8.2x5.8 | 79x63 |
| 27601863041 | 125x63 | 11.4x5.8 | 87x63 |
| 27601863042 | 125x90 | 11.4x8.2 | 87x79 |
| 27601863045 | 140x90 | 12.7x8.2 | 92x79 |
| 27601863049 | 160x63 | 14.6x5.8 | 98x63 |
| 27601863050 | 160x90 | 14.6x8.2 | 98x79 |
| 27601863052 | 160x125 | 14.6x11.4 | 98x87 |
| 27601863058 | 180x90 | 16.4x8.2 | 105x79 |
| 27601863060 | 180x125 | 16.4x11.4 | 105x87 |
| 27601863073 | 225x90 | 20.5x8.2 | 120x79 |
| 27601863074 | 225x125 | 20.5x11.4 | 120x87 |
| 27601863076 | 225x180 | 20.5x16.4 | 120x105 |
| 27601863077 | 250x125 | 22.7x11.4 | 129x87 |
| 27601863078 | 250x180 | 22.7x16.4 | 129x105 |
| 27601863079 | 280x110 | 25.4x10.0 | 139x82 |
| 27601863080 | 315x180 | 28.6x16.4 | 150x105 |
| 27601863081 | 315x200 | 28.6x18.2 | 150x112 |

L x L1= shrink-fit lengths in accordance with UNI EN 1555/3

5. 	REDUCTION

5.1. 	Reduction SDR 17 (S8)

| Code material | OD x od mm | Thickness mm | L x L1 mm |
| --- | --- | --- | --- |
| 27601872031 | 110x90 | 6.6x5.4 | 82x79 |
| 27601872042 | 125x90 | 7.4x5.4 | 87x79 |
| 27601872044 | 125x110 | 7.4x6.6 | 87x82 |
| 27601872047 | 140x125 | 8.3x7.4 | 92x87 |
| 27601872050 | 160x90 | 9.5x5.4 | 98x79 |
| 27601872052 | 160x125 | 9.5x7.4 | 98x87 |
| 27601872056 | 180x90 | 10.7x5.4 | 105x79 |
| 27601872058 | 180x125 | 10.7x7.4 | 105x87 |
| 27601872060 | 180x160 | 10.7x9.5 | 105x98 |
| 27601872065 | 200x180 | 11.9x10.7 | 112x105 |
| 27601872072 | 225x90 | 13.4x5.4 | 120x79 |
| 27601872074 | 225x125 | 13.4x7.4 | 120x87 |
| 27601872078 | 225x180 | 13.4x10.7 | 120x105 |
| 27601872079 | 225x200 | 13.4x11.9 | 120x112 |
| 27601872081 | 250x225 | 14.8x13.4 | 129x120 |
| 27601872083 | 280x200 | 16.6x11.9 | 139x112 |
| 27601872084 | 280x250 | 16.6x14.8 | 139x129 |
| 27601872085 | 315x225 | 18.7x13.4 | 150x120 |
| 27601872086 | 315x250 | 18.7x14.8 | 150x129 |

L x L1= shrink-fit length in accordance with UNI EN 1555/3

5.2. 	Reduction SDR 11 (S5)

| Material code | OD x od mm | Thickness mm | L x L1 mm |
| --- | --- | --- | --- |
| 27601871025 | 75x63 | 6.8x5.8 | 70x63 |
| 27601871026 | 90x50 | 8.2x4.6 | 79x55 |
| 27601871028 | 90x63 | 8.2x5.8 | 79x63 |
| 27601871029 | 90x75 | 8.2x6.8 | 79x70 |
| 27601871030 | 110x50 | 10x4.6 | 82x55 |
| 27601871031 | 110x90 | 10x8.2 | 82x79 |
| 27601871041 | 125x63 | 11.4x5.8 | 87x63 |
| 27601871043 | 125x75 | 11.4x6.8 | 87x70 |
| 27601871042 | 125x90 | 11.4x8.2 | 87x79 |
| 27601871044 | 125x110 | 11.4x10 | 87x82 |
| 27601871045 | 140x125 | 12.7x11.4 | 92x87 |
| 27601871050 | 160x90 | 14.6x8.2 | 98x79 |
| 27601871052 | 160x125 | 14.6x11.4 | 98x87 |
| 27601871056 | 180x90 | 16.4x8.2 | 105x79 |
| 27601871058 | 180x125 | 16.4x11.4 | 105x87 |
| 27601871060 | 180x160 | 16.4x14.6 | 105x98 |
| 27601871065 | 200x180 | 18.2x16.4 | 112x105 |
| 27601871072 | 225x90 | 20.5x8.2 | 120x79 |
| 27601871074 | 225x125 | 20.5x11.4 | 120x87 |
| 27601871078 | 225x180 | 20.5x16.4 | 120x105 |
| 27601871079 | 225x200 | 20.5x18.2 | 120x112 |
| 27601871080 | 250x180 | 22.7x16.4 | 129x105 |
| 27601871081 | 250x225 | 22.7x20.5 | 129x120 |
| 27601871083 | 280x200 | 25.4x18.2 | 139x112 |
| 27601871084 | 280x250 | 25.4x22.7 | 139x129 |
| 27601871085 | 315x225 | 28.6x20.5 | 150x120 |
| 27601871086 | 315x250 | 28.6x22.7 | 150x129 |

L x L1= shrink-fit length in accordance with UNI EN 1555/3

6. 	BUTT-END CAP

6.1. 	Butt-end cap SDR 17 (S8)

| Material code | OD mm | Thickness mm | Min L mm |
| --- | --- | --- | --- |
| 27601878027 | 90 | 5.4 | 79 |
| 27601878030 | 110 | 6.6 | 82 |
| 27601878033 | 125 | 7.4 | 87 |
| 27601878036 | 140 | 8.3 | 92nd |
| 27601878039 | 160 | 9.5 | 98 |
| 27601878042 | 180 | 10.7 | 105 |
| 27601878045 | 200 | 11.9 | 112 |
| 27601878048 | 225 | 13.4 | 120 |
| 27601878051 | 250 | 14.8 | 129 |
| 27601878054 | 280 | 16.6 | 139 |
| 27601878057 | 315 | 18.7 | 150 |

6.2. 	Butt-end cap SDR 11 (S5)

| Material code | OD mm | Thickness mm | Min L mm |
| --- | --- | --- | --- |
| 27601877027 | 90 | 8.2 | 79 |
| 27601877030 | 110 | 10.0 | 82 |
| 27601877033 | 125 | 11.4 | 87 |
| 27601877036 | 140 | 12.7 | 92nd |
| 27601877039 | 160 | 14.6 | 98 |
| 27601877042 | 180 | 16.4 | 105 |
| 27601877045 | 200 | 18.2 | 112 |
| 27601877048 | 225 | 20.5 | 120 |
| 27601877051 | 250 | 22.7 | 129 |
| 27601877054 | 280 | 25.4 | 139 |
| 27601877057 | 315 | 28.7 | 150 |

L = shrink-fit length in accordance with UNI EN 1555/3

##### APPENDIX 3

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN ISO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ............................................................................................................................................................................

Address of the issuer: .......................................................................................................................................................................

(3)	Subject of the declaration: ……........................................................................................................................................................

.......................................................................................................................................................................................................................

……………………………….......................................................................................................................................................................

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(4)	S.T.V.F.C.  1800300 POLYETHYLENE FITTINGS AND SPECIAL PIECES FOR 	Edition 5 of 30/09/2022

METHANE PIPELINES

Additional information:

(5) 	...........................................................................................................................................................................................................

...........................................................................................................................................................................................................

...........................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(6) 	.........................................................

......................................................................................................................

(Name and position) (Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- List all the products for which approval for company use is requested (name, type, model), stating any codes assigned by the Supplier itself and, where existing, the relevant material codes assigned by Italgas Reti.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.