- “TECHNICAL SPECIFICATION FOR EVALUATION, SUPPLY AND TESTING”

- S.T.V.F.C. 17AA300

Steel fittings

| Compiled by | APT-ATECH-NORM | MARELLA MANUELE |
| --- | --- | --- |
|  | APT-ATECH-NORM | NORDIO IVANO |
| Checked by | APT-ATECH-NORM | CIMINO SALVATORE |
| Checked by | PROMA-MATMA | SCOTTO ENRICO |
| Checked by | BDT | AMBROSI LEONARDO |
| Checked by | PROMA/CMMAT | FASSINO SILVIO |
| Checked by | HSEQ | LIMONTA AGOSTINO MASSIMO |
| Approved by | APT-ATECH | GHIBAUDO CLAUDIO |

SUMMARY

1	PRELIMINARY INFORMATION	4

1.1	Cancels and replaces	4

1.2	Reason for issue	4

1.3	Definitions	4

2	PURPOSE AND FIELD OF APPLICATION	4

2.1	Purpose	4

2.2	Field of application	5

3	SPECIFICATIONS	5

4	TECHNICAL CHARACTERISTICS	5

4.1	Pressure equipment	5

4.2	Seamless, steel butt-weld fittings for LP and MP gas installations	6

4.2.1	Metallurgical and mechanical properties	6

4.2.2	Manufacturing process	6

4.2.3	Dimensions and tolerances	6

4.2.4	Fitting end finish	13

4.2.5	Corrosion protection	14

4.3	Seamless, steel butt-weld fittings for HP gas installations	14

4.3.1	Metallurgical and mechanical properties	14

4.3.2	Manufacturing process	14

4.3.3	Dimensions and tolerances	14

4.3.4	Fitting end finish	19

4.3.5	Corrosion protection	20

5	MARKING	20

6	TYPE TEST	20

7	TEST CONDITIONS	21

7.1	Right of the Client	21

8	CONDITIONS OF SUPPLY	21

9	DOCUMENTATION REQUIRED FROM THE SUPPLIER	21

9.1	Supplier	21

9.2	Documents to be submitted	21

9.3	Test Documentation	21

9.4	Supply Documentation	22

10	REFERENCE STANDARDS	22

11	APPENDICES	22

Appendix 1	23

# PRELIMINARY INFORMATION

The c defined in this Technical Specification for Evaluation, Supply and Testing (Italian acronym S.T.V.F.C.) must comply with the current reference standards and the construction and technical requirements of the Decrees of 16.04.2008 and 17.04.2008.

## Cancels and replaces

This specification cancels and replaces S.T.V. 17AA300, edition 1, dated 15 June 2017 - “Steel fittings”;

## Reason for issue

The update of the Technical Specification 17AA300 was required to adopt the new coated and non-coated pipe diameters ND 65 (2.5") and ND 125 (5").

Company departments mentioned in the document

- PROMA-CMMAT = Category Manager Materials

## Definitions

The technical definitions contained in this specification conform to those of the standards listed in point 10  “Reference standards”.

# PURPOSE AND FIELD OF APPLICATION

## Purpose

This Specification determines the technical characteristics of steel butt-weld fittings for gas plants operating in:

- 7th Type (LP):	                                                0.004 MPa ( 0.04 bar);

- 6th-5th-4th-3rd Type (MPA, MPB and MPC):	0.05 MPa (0.5 bar) < P 1.2 MPa (12 bar);

- 2nd-1st Type (HP):                                              1.2 MPa (12 bar) < P  7.5 MPa (75 bar).

## Field of application

It applies whenever steel fittings covered by this specification must be authorised for company use, produced by a new potential Supplier or by an existing one.

This specification regulates the supply of fittings with nominal diameters up to ND 600 (24") for LP and MP and up to ND 500 (20") for HP.

# SPECIFICATIONS

- These technical specifications must be understood as an integral part of the "ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS."

- This specification contains the minimum technical requirements demanded by Italgas Reti based on the reference Legislative and Technical Standards.

- It is the Supplier's responsibility to ensure that the products supplied fully comply with the provisions of this technical specification and the applicable standards.

- If the products in question are supplied by an installer, the installer must document their compliance as required under 9 “Documentation required from the Supplier”.

- It is the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. sharp edges or incorrect directions for use and maintenance), which may jeopardise the health and safety of the Client's workers in relation to the provisions of Italian Legislative Decree no. 81/08, as amended and supplemented.

- For any technical and operational aspects that conflict with or are not mentioned in this technical specification but that nevertheless pertain to the design, installation, maintenance and use of the products themselves, it is the Supplier's responsibility to refer to the regulations in force.

# TECHNICAL CHARACTERISTICS

The steel fittings in this specification must meet the requirements and provide the guarantees to be declared compliant with the current reference standards and with the construction and technical requirements contained in the Ministerial Decree of 16 April 2008 and related updates.

The technical requirements requested by Italgas Reti and those specified by the reference standards on steel fittings are indicated below for each type of fitting.

## Pressure equipment

Steel fittings used in the construction of natural gas distribution systems operating at a pressure greater than 0.5 bar must comply with the provisions of Legislative Decree no. 93 of 25 February 2000, as amended. (Directive 2014/68/EU).

In accordance with the 2014/68/EU Directive, the following harmonised standards in particular must be applied as far as relevant:

- UNI EN 10253-2 - "Butt-welding pipe fittings - Non-alloy steels and ferritic alloy steels with specific testing requirements".

## Seamless, steel butt-weld fittings for LP and MP gas installations

As regards the construction of the ELBOW, TEE, REDUCED TEE, CONCENTRIC REDUCER and ELLIPSOIDAL CAP, the characteristics and reference standards must correspond, for steel material, to the following:

### Metallurgical and mechanical properties

  - Steel with a unit yield strength of 235 N/mm2 according to UNI EN 10253-2 (P235TR2 or P235GH steel);

or alternatively:

  - Grade B steel with a unit yield strength of 240 N/mm2 according to ASTM A 234 WPB.

The use of steel P235TR2 no. 1.0255 with a unit yield strength of 235 N/mm2 in accordance with EN 10216-1 is only permissible for the manufacture of hot-formed ELBOWS and for OD  219.1.

### Manufacturing process

Fittings must be made from seamless pipes, forged parts or sheet metal by forging, extrusion or machining and must be supplied normalised. Fittings made by welding or from welded pipes are not permitted. Fittings subjected to hardening and tempering heat-treatments are also not permitted. The forged pipes, sheet-metal and parts to be used for the manufacture of fittings must be made from quality steel, produced in the Martin-Siemens or electric furnace or using the LD oxygen converter process.

### Dimensions and tolerances

The dimensions and tolerances required for the fittings shown in Table 1 below, indicating the name and respective material code, must comply with the requirements of standard UNI EN 10253-1, as shown in Table 2 below "Dimensions of steel fittings for LP and MP". Fitting thicknesses for ND  400 must comply with UNI EN 10253-1, and for ND 500 and 600 with ANSI B 36-10 schedule 20.

Table 1- Steel Fittings Designation for LP and MP

| Drawing | Name | ND | Material Code |
| --- | --- | --- | --- |
|  | 45° elbow (type 3 D) R = 1.5 ND | 20 25 40 50 65 80 100 125 150 200 250 300 350 400 500 600 | 33501770710 33501770712 33501770716 33501770720 33501770722 33501770726 33501770730 33501770732 33501770736 33501770741 33501770745 33501770749 33501770750 33501770752 33501770754 33501770756 |
|  | 90° elbow (type 3 D) R = 1.5 ND | 20 25 40 50 65 80 100 125 150 200 250 300 350 400 500 600 | 33501772010 33501772012 33501772016 33501772020 33501772022 33501772026 33501772030 33501772032 33501772136 33501772141 33501772145 33501772149 33501772150 33501772152 33501772156 33501772159 |
|  | 45° elbow (type 5 D) R = 5 ND | 20 25 40 50 65 80 100 125 150 200 250 300 350 400 500 | 33501772320 33501772321 33501772322 33501772324 33501772325 33501772326 33501772330 33501772333 33501772636 33501772641 33501772645 33501772649 33501772650 33501772652 33501772654 |

| Drawing | Name | ND | Material Code |
| --- | --- | --- | --- |
|  | Ellipsoidal cap | 20 25 40 50 65 80 100 125 150 200 250 300 350 400 500 600 | 33501778700 33501778701 33501778703 33501778704 33501778705 33501778706 33501778708 33501778709 33501778710 33501778712 33501778714 33501778716 33501778718 33501778720 33501778724 33501778726 |
|  | Reduced tee | 40x25 50x40 50x25 65x40 65x50 80x50 80x40 100x80 100x50 125x80 125x100 150x100 150x80 200x150 200x100 250x200 250x150 300x250 300x200 300x150 350x300 350x250 350x200 400x350 400x300 400x250 500x400 500x350 600x500 600x400 | 33501774218 33501774222 33501774224 33501774227 33501774228 33501774225 33501774226 33501774234 33501774236 33501774240 33501774241 33501774247 33501774248 33501774252 33501774254 33501774258 33501774259 33501774261 33501774262 33501774263 33501774267 33501774268 33501774269 33501774273 33501774274 33501774275 33501774282 33501774283 33501774286 33501774288 |

| Drawing | Name | ND | Material Code |  |
| --- | --- | --- | --- | --- |
|  | Concentric reducer Shape 2 | 40x20 25x20 40x25 50x40 50x25 65x50 65x40 80x65 80x50 80x40 100x80 100x50 125x100 125x80 150x125 150x100 150x80 200x150 200x100 250x200 250x150 300x250 300x200 300x150 350x300 350x250 350x200 400x350 400x300 400x250 500x350 500x400 600x500 600x400 | 33501776210 33501776212 33501776215 33501776216 33501776218 33501776219 33501776221 33501776224 33501776225 33501776226 33501776234 33501776236 33501776230 33501776231 33501776246 33501776247 33501776248 33501776252 33501776254 33501776258 33501776259 33501776261 33501776262 33501776263 33501776264 33501776268 33501776269 33501776270 33501776271 33501776272 33501776277 33501776278 33501776282 33501776284 |  |
|  | Tee | 20 25 40 50 65 80 100 125 150 200 250 300 350 400 500 600 | 33501774110 33501774112 33501774116 33501774120 33501774122 33501774126 33501774130 33501774132 33501774136 33501774141 33501774145 33501774149 33501774150 33501774152 33501774156 33501774158 |  |

Table 2- Steel Fitting Sizes for LP and MP

|  | Designation |  |  |  |  |  | Dimensions |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ND x nd |  |  |  |  |  | OD x od |  |  | T | t | A | B | C | D | E | F |
|  | mm |  |  | in |  |  | mm |  |  | mm | mm | mm | mm | mm | mm | mm | mm |
|  | 20 |  |  | ¾ |  |  | 26.9 |  |  | 2.3 | – | 29 | 95 | 29 | – | – | 25 |
|  | 25 |  |  | 1 |  |  | 33.7 |  |  | 2.6 | – | 38 | 127 | 38 | – | – | 38 |
|  | 25 | x | 20 | 1 | x | ¾ | 33.7 | x | 26.9 | 2.6 | 2.3 | – | – | 38 | 38 | 51 | – |
|  | 40 |  |  | 1½ |  |  | 48.3 |  |  | 2.6 | – | 57 | 190 | 57 | – | – | 38 |
|  | 40 | x | 25 | 1½ | x | 1 | 48.3 | x | 33.7 | 2.6 | 2.6 | – | – | 57 | 57 | 64 | – |
|  | 40 | x | 20 | 1½ | x | ¾ | 48.3 | x | 26.9 | 2.6 | 2.3 | – | – | – | – | 64 | – |
|  | 50 |  |  | 2 |  |  | 60.3 |  |  | 2.9 | – | 76 | 254 | 64 | – | – | 38 |
|  | 50 | x | 40 | 2 | x | 1½ | 60.3 | x | 48.3 | 2.9 | 2.6 | – | – | 64 | 60 | 76 | – |
|  | 50 | x | 25 | 2 | x | 1 | 60.3 | x | 33.7 | 2.9 | 2.6 | – | – | 64 | 51 | 76 | – |
|  | 65 |  |  | 2½ |  |  | 76.1 |  |  | 2.9 | - | 95 | 317 | 76 | - | - | 38 |
|  | 65 | x | 50 | 2½ | x | 2 | 76.1 | x | 60.3 | 2.9 | 2.9 |  |  | 76 | 70 | 90 | - |
|  | 65 | x | 40 | 2½ | x | 1½ | 76.1 | x | 48.3 | 2.9 | 2.6 | - | - | 76 | 67 | 90 | -- |
|  | 80 |  |  | 3 |  |  | 88.9 |  |  | 3.2 | – | 114 | 381 | 86 | – | – | 51 |
|  | 80 | x | 65 | 3 | x | 2½ | 88.9 | x | 76.1 | 3.2 | 2.9 | – | – | - | - | 90 | – |
|  | 80 | x | 50 | 3 | x | 2 | 88.9 | x | 60.3 | 3.2 | 2.9 | – | – | 86 | 76 | 90 | – |
|  | 80 | x | 40 | 3 | x | 1½ | 88.9 | x | 48.3 | 3.2 | 2.6 | – | – | 86 | 73 | 90 | – |
|  | 100 |  |  | 4 |  |  | 114.3 |  |  | 3.6 | – | 152 | 508 | 105 | – | – | 64 |
|  | 100 | x | 80 | 4 | x | 3 | 114.3 | x | 88.9 | 3.6 | 3.2 | – | – | 105 | 98 | 102 | – |
|  | 100 | x | 50 | 4 | x | 2 | 114.3 | x | 60.3 | 3.6 | 2.9 | – | – | 105 | 89 | 102 | – |
|  | 125 |  |  | 5 |  |  | 139.7 |  |  | 4.0 |  | 190 | 635 | 124 | - | - | 76 |
|  | 125 | x | 100 | 5 | x | 4 | 139.7 | x | 114.3 | 4.0 | 3.6 | - | - | 124 | 117 | 127 |  |
|  | 125 | x | 80 | 5 | x | 3 | 139.7 | x | 88.9 | 4.0 | 3.2 | - | - | 124 | 111 | 127 |  |
|  | 150 |  |  | 6 |  |  | 168.3 |  |  | 4.5 | – | 229 | 762 | 143 | – | – | 89 |
|  | 150 | x | 125 | 6 | x | 5 | 168.3 | x | 139.7 | 4.5 | 4.0 | - | - | - | - | 140 | - |
|  | 150 | x | 100 | 6 | x | 4 | 168.3 | x | 114.3 | 4.5 | 3.6 | – | – | 143 | 130 | 140 | – |
|  | 150 | x | 80 | 6 | x | 3 | 168.3 | x | 88.9 | 4.5 | 3.2 | – | – | 143 | 124 | 140 | – |
|  | 200 |  |  | 8 |  |  | 219.1 |  |  | 6.3 | – | 305 | 1016 | 178 | – | – | 102 |
|  | 200 | x | 150 | 8 | x | 6 | 219.1 | x | 168.3 | 6.3 | 4.5 | – | – | 178 | 168 | 152 | – |
|  | 200 | x | 100 | 8 | x | 4 | 219.1 | x | 114.3 | 6.3 | 3.6 | – | – | 178 | 156 | 152 | – |
|  | 250 |  |  | 10 |  |  | 273 |  |  | 6.3 | – | 381 | 1270 | 216 | – | – | 127 |
|  | 250 | x | 200 | 10 | x | 8 | 273 | x | 219.1 | 6.3 | 6.3 | – | – | 216 | 203 | 178 | – |
|  | 250 | x | 150 | 10 | x | 6 | 273 | x | 168.3 | 6.3 | 4.5 | – | – | 216 | 194 | 178 | – |
|  | 300 |  |  | 12 |  |  | 323.9 |  |  | 7.1 | – | 457 | 1524 | 254 | – | – | 152 |
|  | 300 | x | 250 | 12 | x | 10 | 323.9 | x | 273 | 7.1 | 6.3 | – | – | 254 | 241 | 203 | – |
|  | 300 | x | 200 | 12 | x | 8 | 323.9 | x | 219.1 | 7.1 | 6.3 | – | – | 254 | 229 | 203 | – |
|  | 300 | x | 150 | 12 | x | 6 | 323.9 | x | 168.3 | 7.1 | 4.5 | – | – | 254 | 219 | 203 | – |
|  | 350 |  |  | 14 |  |  | 355.6 |  |  | 8.0 | – | 533 | 1778 | 279 | – | – | 165 |
|  | 350 | x | 300 | 14 | x | 12 | 355.6 | x | 323.9 | 8.0 | 7.1 | – | – | 279 | 270 | 330 | – |
|  | 350 | x | 250 | 14 | x | 10 | 355.6 | x | 273 | 8.0 | 6.3 | – | – | 279 | 257 | 330 | – |
|  | 350 | x | 200 | 14 | x | 8 | 355.6 | x | 219.1 | 8.0 | 6.3 | – | – | 279 | 248 | 330 | – |

| Designation |  |  |  |  |  | Dimensions |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ND x nd |  |  |  |  |  | OD x od |  |  | T | t | A | B | C | D | E | F |
| mm |  |  | in |  |  | mm |  |  | mm | mm | mm | mm | mm | mm | mm | mm |
| 400 |  |  | 16 |  |  | 406.4 |  |  | 8.8 | – | 610 | 2032 | 305 | – | – | 178 |
| 400 | x | 350 | 16 | x | 14 | 406.4 | x | 355.6 | 8.8 | 8.0 | – | – | 305 | 305 | 356 | – |
| 400 | x | 300 | 16 | x | 12 | 406.4 | x | 323.9 | 8.8 | 7.1 | – | – | 305 | 295 | 356 | – |
| 400 | x | 250 | 16 | x | 10 | 406.4 | x | 273 | 8.8 | 6.3 | – | – | 305 | 283 | 356 | – |
| 500 |  |  | 20 |  |  | 508 |  |  | 9.5 | – | 762 | 2540 | 381 | – | – | 229 |
| 500 | x | 400 | 20 | x | 16 | 508 | x | 406.4 | 9.5 | 8.8 | – | – | 381 | 356 | 508 | – |
| 500 | x | 350 | 20 | x | 14 | 508 | x | 355.6 | 9.5 | 8 | – | – | 381 | 356 | 508 | – |
| 600 |  |  | 24 |  |  | 610 |  |  | 9.5 | – | 914 | 3050 | 432 | – | – | 267 |
| 600 | x | 500 | 24 | x | 20 | 610 | x | 508 | 9.5 | 9.5 | – | – | – | – | 508 | – |
| 600 | x | 400 | 24 | x | 16 | 610 | x | 406.4 | 9.5 | 8.8 | – | – | 432 | 406 | 508 | – |

NOTES:  nd, od, t : dimensions referred to reduced diameter

Table 3 - Preparation of steel fitting ends for LP and MP

|  | ND |  | T/t | T1 | Ends |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | mm | in | mm | mm | flat | chamfered | tapered |
|  | 20 | ¾ | 2.3 | 2.3 |  | – | – |
|  | 25 | 1 | 2.6 | 2.6 |  | – | – |
|  | 40 | 1½ | 2.6 | 2.6 |  | – | – |
|  | 50 | 2 | 2.9 | 2.9 |  | – | – |
|  | 65 | 2½ | 3.2 | 3.2 |  |  |  |
|  | 80 | 3 | 3.2 | 3.2 |  | – | – |
|  | 100 | 4 | 3.6 | 3.6 | – |  | – |
|  | 125 | 5 | 3.6 | 3.6 | - |  | - |
|  | 150 | 6 | 4.5 | 4.0 | – |  |  |
|  | 200 | 8 | 6.3 | 5.0 | – |  |  |
|  | 250 | 10 | 6.3 | 5.6 | – |  |  |
|  | 300 | 12 | 7.1 | 5.6 | – |  |  |
|  | 350 | 14 | 8 | 6.3 | – |  |  |
|  | 400 | 16 | 8.8 | 6.3 | – |  |  |
|  | 500 | 20 | 9.5 | 6.3 | – |  |  |
|  | 600 | 24 | 9.5 | 7.1 | – |  |  |

NOTES		ND  400 thicknesses T/t according to UNI EN 10253-1

ND 500 and 600 thicknesses T/t according to ANSI B36.10 - Schedule 20

- T1: thickness of the weld end of the fitting

### Fitting end finish

Unless otherwise specified in the order, the ends of fittings must be supplied adequately prepared (see Table 3) at both ends, free of harmful burrs, according to the reference standards below.

| FLAT (UNI ISO 6761) T1 £ mm 3.2 | CHAMFERED (UNI ISO 6761) T1 > mm 3.2 |
| --- | --- |
|  | C = 1.6 ± 0.8 a = 37.5° ± 2.5° |

CHAMFERED AND TAPERED (ANSI B 16.9) for ND 150 ¸ 600

| Tolerance on end thickness T1 |  |
| --- | --- |
| with respect to wall thickness T |  |
| max (- 12.5 %) of T |  |

C = 1.6 ± 0.8 a = 37.5° ± 2.5° b = £ 18°

### Corrosion protection

The outer surface of the fittings must be adequately protected against corrosion by applying anti-rust paint.

## Seamless, steel butt-weld fittings for HP gas installations

As regards the construction of the BEND, TEE, REDUCED TEE, CONCENTRIC REDUCER and ELLIPSOIDAL CAP, the characteristics and reference standards must correspond, for steel material, to the following:

### Metallurgical and mechanical properties

  - High-strength carbon steel according to MSS-SP-75 for gas pipelines grade WPHY52 with unit yield strength 358 N/mm2 according to ANSI B 31.8.

### Manufacturing process

Fittings must be made from seamless pipes, forged parts or sheet metal by forging, extrusion or machining and must be supplied normalised. Fittings made by welding or from welded pipes are not permitted. Fittings subjected to hardening and tempering heat-treatments are also not permitted. The forged pipes, sheet-metal and parts to be used for the manufacture of fittings must be made from killed quality steel, produced in the Martin-Siemens or electric furnace or using the LD oxygen converter process.

### Dimensions and tolerances

The dimensions and tolerances required for the fittings shown in the following Table 4 "Designation of steel fittings for HP", indicating both the designation and the respective Material Code, must comply with the:

- ANSI B 36.10 schedule 40 standard for the selection of nominal wall thicknesses of the fitting.

- ANSI B 16.9 standard for the preparation of butt weld ends,

as shown in Table 5 below - Dimensions of steel fittings for HP (12 < P  75 bar).

Table 4 - Steel Fittings Designation for HP

| Drawing | Name | ND | Material Code |
| --- | --- | --- | --- |
|  | 45° BEND (type 3 D) R = 1.5 ND | 80 100 125 150 200 250 300 350 400 500 | 33501770854 33501770856 33501770857 33501770858 33501770860 33501770862 33501770864 33501770865 33501770866 33501770868 |
|  | 90° BEND (type 3 D) R = 1.5 ND | 80 100 125 150 200 250 300 350 400 500 | 33501772172 33501772175 33501772176 33501772179 33501772181 33501772183 33501772184 33501772185 33501772187 33501772191 |
|  | 45° BEND (type 5 D) R = 5 ND | 80 100 125 150 200 250 300 350 400 500 | 33501772845 33501772847 33501772848 33501772849 33501772851 33501772853 33501772854 33501772855 33501772857 33501772861 |

cont.

| Drawing | Name | ND | Material Code |
| --- | --- | --- | --- |
|  | Ellipsoidal cap | 80 100 125 150 200 250 300 350 400 500 | 33501778606 33501778608 33501778609 33501778610 33501778612 33501778614 33501778616 33501778618 33501778620 33501778624 |
|  | Reduced tee | 80x50 80x40 100x80 100x50 125x100 125x80 150x100 150x80 200x150 200x100 250x200 250x150 250x100 300x250 300x200 300x150 350x300 350x250 350x200 350x150 400x350 400x300 400x250 400x200 400x150 500x400 500x350 500x300 500x250 | 33501774347 33501774348 33501774350 33501774354 33501774356 33501774357 33501774360 33501774362 33501774364 33501774366 33501774368 33501774370 33501774372 33501774374 33501774376 33501774378 33501774380 33501774382 33501774384 33501774386 33501774388 33501774390 33501774392 33501774394 33501774396 33501774410 33501774412 33501774414 33501774416 |

cont.

| Drawing | Name | ND | Material Code |  |
| --- | --- | --- | --- | --- |
|  | Concentric reducer | 80x50 80x40 100x80 100x50 125x100 125x80 150x100 150x80 200x150 200x100 250x200 250x150 250x100 300x250 300x200 300x150 350x300 350x250 350x150 400x350 400x300 400x250 400x200 500x400 500x350 500x300 | 33501776604 33501776606 33501776608 33501776610 33501776612 33501776613 33501776614 33501776616 33501776618 33501776620 33501776622 33501776624 33501776626 33501776628 33501776630 33501776632 33501776634 33501776636 33501776640 33501776642 33501776644 33501776646 33501776648 33501776660 33501776662 33501776664 |  |
|  | Tee | 80 100 125 150 200 250 300 350 400 500 | 33501774323 33501774325 33501774327 33501774329 33501774331 33501774333 33501774335 33501774336 33501774337 33501774339 |  |

Table 5 - Dimensions of steel fittings for HP (12 < P  75 bar).

|  | Designation |  |  |  |  |  | Dimensions |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ND x nd |  |  |  |  |  | OD x od |  |  | T | t | A | B | C | D | E | F |
|  | mm |  |  | in |  |  | mm |  |  | mm | mm | mm | mm | mm | mm | mm | mm |
|  | 80 |  |  | 3 |  |  | 88.9 |  |  | 5.5 | – | 114 | 381 | 86 | – | – | 51 |
|  | 80 | x | 65 | 3 | x | 2½ | 88.9 | x | 76.1 | 5.5 | 5.1 | – | – | – | – | 89 | – |
|  | 80 | x | 50 | 3 | x | 2 | 88.9 | x | 60.3 | 5.5 | 3.9 | – | – | 86 | 76 | 89 | – |
|  | 80 | x | 40 | 3 | x | 1½ | 88.9 | x | 48.3 | 5.5 | 3.7 | – | – | 86 | 73 | 89 | – |
|  | 100 |  |  | 4 |  |  | 114.3 |  |  | 6.0 | – | 152 | 508 | 105 | – | – | 64 |
|  | 100 | x | 80 | 4 | x | 3 | 114.3 | x | 88.9 | 6.0 | 5.4 | – | – | 105 | 98 | 102 | – |
|  | 100 | x | 50 | 4 | x | 2 | 114.3 | x | 60.3 | 6.0 | 3.9 | – | – | 105 | 89 | 102 | – |
|  | 125 |  |  | 5 |  |  | 139.7 |  |  | 6.6 | - | 190 | 635 | 124 | - | - | 76 |
|  | 125 | x | 100 | 5 | x | 4 | 139.7 | x | 114.3 | 6.6 | 6.0 | - | - | 124 | 117 | 127 | - |
|  | 125 | x | 80 | 5 | x | 3 | 139.7 | x | 88.9 | 6.6 | 5.4 | - | - | 124 | 111 | 127 | - |
|  | 150 |  |  | 6 |  |  | 168.3 |  |  | 7.1 | – | 229 | 762 | 143 | – | – | 89 |
|  | 150 | x | 100 | 6 | x | 4 | 168.3 | x | 114.3 | 7.1 | 6.0 | – | – | 143 | 130 | 140 | – |
|  | 150 | x | 80 | 6 | x | 3 | 168.3 | x | 88.9 | 7.1 | 5.5 | – | – | 143 | 124 | 140 | – |
|  | 200 |  |  | 8 |  |  | 219.1 |  |  | 8.1 | – | 305 | 1016 | 178 | – | – | 102 |
|  | 200 | x | 150 | 8 | x | 6 | 219.1 | x | 168.3 | 8.1 | 7.1 | – | – | 178 | 168 | 152 | – |
|  | 200 | x | 100 | 8 | x | 4 | 219.1 | x | 114.3 | 8.1 | 6.0 | – | – | 178 | 156 | 152 | – |
|  | 250 |  |  | 10 |  |  | 273 |  |  | 9.3 | – | 381 | 1270 | 216 | – | – | 152 |
|  | 250 | x | 200 | 10 | x | 8 | 273 | x | 219.1 | 9.3 | 8.1 | – | – | 216 | 203 | 178 | – |
|  | 250 | x | 150 | 10 | x | 6 | 273 | x | 168.3 | 9.3 | 7.1 | – | – | 216 | 194 | 178 | – |
|  | 300 |  |  | 12 |  |  | 323.9 |  |  | 10.3 | – | 457 | 1524 | 254 | – | – | 178 |
|  | 300 | x | 250 | 12 | x | 10 | 323.9 | x | 273 | 10.3 | 9.3 | – | – | 254 | 241 | 203 | – |
|  | 300 | x | 200 | 12 | x | 8 | 323.9 | x | 219.1 | 10.3 | 8.1 | – | – | 254 | 229 | 203 | – |
|  | 300 | x | 150 | 12 | x | 6 | 323.9 | x | 168.3 | 10.3 | 7.1 | – | – | 254 | 219 | 203 | – |
|  | 350 |  |  | 14 |  |  | 355.6 |  |  | 11.1 | – | 533 | 1778 | 279 | – | – | 191 |
|  | 350 | x | 300 | 14 | x | 12 | 355.6 | x | 323.9 | 11.1 | 10.3 |  | – | 279 | 270 | 330 | – |
|  | 350 | x | 250 | 14 | x | 10 | 355.6 | x | 273 | 11.1 | 9.3 | – | – | 279 | 257 | 330 | – |
|  | 350 | x | 200 | 14 | x | 8 | 355.6 | x | 219.1 | 11.1 | 8.1 | – | – | 279 | 248 | 330 | – |
|  | 400 |  |  | 16 |  |  | 406.4 |  |  | 12.7 | – | 610 | 2032 | 305 | – | – | 203 |
|  | 400 | x | 350 | 16 | x | 14 | 406.4 | x | 355.6 | 12.7 | 11.1 | – | – | 305 | 305 | 356 | – |
|  | 400 | x | 300 | 16 | x | 12 | 406.4 | x | 323.9 | 12.7 | 10.3 | – | – | 305 | 295 | 356 | – |
|  | 400 | x | 250 | 16 | x | 10 | 406.4 | x | 273 | 12.7 | 9.3 | – | – | 305 | 283 | 356 | – |
|  | 500 |  |  | 20 |  |  | 508 |  |  | 15.0 | – | 762 | 2540 | 381 | – | – | 254 |
|  | 500 | x | 400 | 20 | x | 16 | 508 | x | 406.4 | 15.0 | 12.7 | – | – | 381 | 356 | 508 | – |
|  | 500 | x | 350 | 20 | x | 14 | 508 | x | 355.6 | 15.0 | 11.1 | – | – | 381 | 356 | 508 | – |

NOTES	:

- nd, od, t : dimensions referred to reduced diameter

Table 6 - Preparation of steel fitting end for HP.

|  | ND |  | T/t | T1 | Ends |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | mm | in | mm | mm | flat | chamfered | tapered |
|  | 80 | 3 | 5.5 | 3.2 | -- |  |  |
|  | 100 | 4 | 6.0 | 3.2 | – |  |  |
|  | 125 | 5 | 6.6 | 4.0 | - |  |  |
|  | 150 | 6 | 7.1 | 4.5 | – |  |  |
|  | 200 | 8 | 8.1 | – | – |  |  |
|  | 250 | 10 | 9.3 | – | – |  |  |
|  | 300 | 12 | 10.3 | – | – |  |  |
|  | 350 | 14 | 11.1 | – | – |  |  |
|  | 400 | 16 | 12.7 | – | – |  |  |
|  | 500 | 20 | 15.0 | – | – |  |  |

NOTES	:

- thicknesses T/t according to ANSI B36. 10

- T1 : thickness of the end prepared for welding the fitting to the steel pipe of minimum thickness for HP;

for HP pipe thicknesses greater than that indicated, the value of T1 will be assessed on a case-by-case basis.

### Fitting end finish

The ends of the fittings must be supplied adequately prepared (see Table 6 "Preparation of steel fittings ends for HP") at the ends according to the standard and with the tolerances indicated below:

CHAMFERED AND TAPERED (ANSI B 16.9) for ND 80 ¸ 150

Tolerance on end thickness T1

with respect to wall thickness T

max (- 12.5 %) of T

C = 1.6 ± 0.8 a = 37.5° ± 2.5° b = £ 18°

CHAMFERED (ANSI B 16.9) for ND 200  500

Tolerance on end thickness T1

with respect to wall thickness T

max (- 12.5 %) of T

C = 1.6 ± 0.8

a = 37.5° ± 2.5°

### Corrosion protection

On the outer surface, all fittings must be coated with anti-rust paint.

# MARKING

Fittings must be marked legibly and with the indications required in point 15 of UNI EN 10253- 2.

# TYPE TEST

Fittings complying with this Technical Specification must be subjected by the Supplier to all the tests indicated in point 12 of UNI EN 10253-2 for steel fittings supplied in accordance with UNI EN 10253.

For WPB-grade steel fittings, the tests must meet the requirements of ASTM A 234.

# TEST CONDITIONS

Italgas Reti reserves the right:

- To be present with its own Inspectors and/or Inspection Companies appointed by the same to carry out tests/checks c/o your plant and at your care and expense, to check the constructive and functional compliance of the materials in accordance with the specifications and/or reference standards.

- To verify, upon receipt and/or under actual conditions of use, the perfect compliance of the goods with the functional technical characteristics expressly indicated in the Contract.

It remains understood that the favourable outcome of our Inspection and checking of the materials shall not release you in any way from your responsibilities and obligations arising from every individual Contract.

## Right of the Client

It is Italgas Reti's right, for each purchase order, to request from the Supplier:

- Further technical and/or graphic documentation,

- additional laboratory and/or field tests,

in order to verify the conformity of the proposed products with this technical specification and the cited standards to which reference is made.

# CONDITIONS OF SUPPLY

Supplier's Standard in compliance with Legislative Decree no. 152 of 3 April 2006 as amended and supplemented.

# DOCUMENTATION REQUIRED FROM THE SUPPLIER

## Supplier

The potential Supplier must be qualified as an ITALGAS Supplier.

## Documents to be submitted

The potential Supplier must submit to the PROMA/CMMAT Department the “Declaration of Conformity” with this technical specification and any specific documents (legislative provisions, applied standards, etc.) to which the supplier refers for the design and construction of the product, in accordance with the requirements of UNI CEI EN ISO/IEC 17050-1 (see the example in APPENDIX 1 to this technical specification).

## Test Documentation

The Supplier must issue a “type 3.1” Inspection Certificate in accordance with UNI EN 10204, which states that the products provided are compliant with the requirements of these specifications and which provides the test results.

Registration of the full production/test documentation completed by the Supplier must be kept (on the basis of legal provisions) for 10 years under its responsibility, and must be made available whenever requested by the Client.

## Supply Documentation

- Documents compliant with Legislative Decree no. 286 of 21 November 2005, as amended and supplemented;

# REFERENCE STANDARDS

- Italian Legislative Decree no. 93 of 25 February 2000, as amended "Implementation of Directive 97/23/EC on pressure equipment and Directive 2014/68/EU on the harmonisation of the laws of the Member States relating to the making available on the market of pressure equipment (recast), providing for its repeal".

- Italian Legislative Decree no. 81 of 9 April 2008, as amended - “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”.

- Italian Legislative Decree no. 152 of 3 April 2006, as amended “Environmental standards”.

- Italian Legislative Decree no. 286 of 21 November 2005, as amended “Provisions for the regulatory reorganisation of the regulated liberalisation of the road haulage business”.

- Ministerial Decree of 16 April 2008 - “Technical regulations for the design, construction, testing, operation and supervision of works and distribution systems and direct lines for natural gas with a density not exceeding 0.8”.

- Ministerial Decree of 17 April 2008 - “Technical regulations for the design, construction, testing, operation and supervision of works and plants for the transmission of natural gas with a density not exceeding 0.8”.

- ASTM A234 – “Standard Specification for piping fittings of wrought carbon steel and alloy steel for moderate and high temperature service”.

- ASME/ANSI B 16.9 – “Factory-made Wrought Butt-Welding Fittings”.

- ASME B16.25 – “Butt-welding Ends”.

- ASME/ANSI B31.8 – “Gas Transmission and Distribution Piping Systems”.

- ASME/ANSI B 36.10 – “Welded and seamless wrought steel pipe”.

- UNI EN 10253-1 - "Butt-weld pipe fittings - Wrought carbon steel for general use and without specific inspection requirements

- UNI EN 10253-2 - "Butt-weld pipe fittings - Non-alloy steels and ferritic alloy steels with specific testing requirements".

- UNI EN 10216-1 - "Seamless steel pipes for pressure purposes - Technical delivery conditions. Non-alloy steel pipes with specified room temperature properties".

- UNI ISO 6761 - "Steel pipes. Preparation of ends of pipes and fittings for welding'.

- UNI CEI EN ISO/IEC 17050-1 - "Conformity assessment - Supplier's declaration of conformity - Part 1: General requirements”.

# APPENDICES

- APPENDIX 1 – “Sample Declaration of Conformity with this technical specification”

## Appendix 1

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN ISO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

(4)	The following products manufactured by us:

| Our material code (5) | Italgas Reti material code (6) |
| --- | --- |
| xxx | 33501770710 |
| xxx | xxx |

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(7)	S.T.V.F.C. 17AA300_2	STEEL FITTINGS	Edition 2 of 30/09/2022

Additional information:

(8) 	...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(9) 	............................................................. 		        ...................................................................................................................

(Name and position) 				               (Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- The “subject” must be unambiguously described so that the declaration of conformity can be referred to the subject in question.

- List all the products for which company use authorisation is being requested.

- For each individual product supplied, state the material code used by the Supplier.

- For each individual product supplied, please quote the material code assigned by Italgas Reti, which can be found in the Italgas Reti reference documents. If there are none, please contact APT-ATECH-NORM.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

Supplier means the party responsible for the design and construction of the products or its legal representative as defined in Legislative Decree no. 206 of 6 September 2005 as amended and supplemented. - "Consumer code, pursuant to Article 7 of Law no. 229 of 29 July 2003."