“TECHNICAL SPECIFICATION FOR EVALUATION, SUPPLY AND TESTING”

S.T.V.F.C. 2321300

End-user pressure reducing units from road pipes with upstream pressure between 0.5 and 5 bar

(P.R.U. 10, 25, 50 and 70 m3/h)

| Compiled by | SERTEC-NORM | LORO SILVIO |
| --- | --- | --- |
| Checked by | SERTEC-NORM | VARESE ENRICO |
| Checked by | PROMA-MATMA | SCOTTO ENRICO |
| Checked by | PROMA/CMMAT | FASSINO SILVIO |
| Checked by | HSEQ | BOLZONI GIANLUCA |
| Checked by | SERTEC-LAB | SALATI EUGENIO |
| Approved by | SERTEC | COMAZZI MARCO |

SUMMARY

1	PRELIMINARY INFORMATION	5

1.1	Cancels and replaces	5

1.2	Reason for issue	5

1.3	Company departments mentioned in the document	5

1.4	definitions	5

2	PURPOSE AND FIELD OF APPLICATION	5

2.1	Purpose	5

2.2	Field of application	5

3	Specifications	6

4	Technical characteristics	6

4.1	Constituent elements and construction characteristics of PRUs	6

4.1.1	Filtration system	7

4.1.2	Pressure regulator	7

4.1.3	Pipes, joints and special parts comprising the 70 Sm3/h frame-mounted PRU:	8

4.1.4	Frame joints for 70 Sm3/h PRUs	8

4.2	Functional characteristics	9

4.2.1	Maximum operating pressure (MOPu)	10

4.2.2	Regulated pressure downstream of the first stage (where applicable)	10

4.2.3	Required regulation pressure OPd	10

4.2.4	Accuracy class	10

4.2.5	Closing overpressure	10

4.2.6	Device for discharge into the atmosphere	10

4.2.7	Safety device	10

4.2.7.1	Dual regulation stage (where applicable)	10

4.2.7.2	Manual-reset locking device for maximum regulated downstream pressure	10

4.2.7.3	Manual-reset locking device for minimum regulated downstream pressure	11

4.3	Technical assessment	11

5	Abatement of ACOUSTIC emissions	11

6	Marking	11

7	TYPE TEST	12

8	DOCUMENTATION required from the supplier	12

8.1	Supplier	12

8.2	Documentation for the company approval process	12

8.2.1	New Supplier	12

8.2.1.1	Standardised products	13

8.2.1.2	Products being standardised	13

8.2.2	Supplier with product already approved for company use	14

8.2.2.1	Standardised products	14

8.2.2.2	Products being standardised	14

8.3	Test Documentation	15

8.4	Supply Documentation	15

8.5	Final Documentation	16

8.5.1	Procedure successfully completed	16

8.5.2	Procedure failed	16

9	TESTS AND INSPECTIONS	16

9.1	Visual and dimensional inspection	17

9.2	Mechanical strength test for 70 Sm3/h frame-mounted PRUs	17

9.3	Pneumatic external leak test for 70 Sm3/h frame-mounted PRUs	18

9.4	Inspection of welded joints on 70 Sm3/h frame-mounted PRUs	18

9.5	Right of the client	19

10	CONDITIONS OF SUPPLY	19

11	REFERENCE STANDARDS	19

12	APPENDICES	21

13	annexes	21

Appendix 1	22

Appendix 2	23

Appendix 3	24

Appendix 3/ a	25

Appendix 3/ b	26

Appendix 3/ c	27

Appendix 3/ d	28

Appendix 3/ e	29

Appendix 3/ f	29

Appendix 4	31

Appendix 5	31

Appendix 6	33

# PRELIMINARY INFORMATION

## Cancels and replaces

This specification cancels and replaces:

- S.T.V. 2321300 edition 2 of October 2007

## Reason for issue

The update of the S.T.V. 2321300 and its reissue in the form of Technical Specifications for Assessment and Supply and Testing (S.T.V.F.C.), became necessary as a result of:

- Issuance of new national and European standards (UNI, CEI and EN);

- New legislative context;

- Inclusion of Supply and Testing Criteria;

## Company departments mentioned in the document

- SERTEC-NORM = Standard

## definitions

The technical definitions contained in this specification conform to those of the standards listed in point 11 “REFERENCE STANDARDS.

# PURPOSE AND FIELD OF APPLICATION

## Purpose

This Technical Specification defines the technical and construction characteristics, the accompanying documentation and the procedures for carrying out the technical inspections for the approval of end-user “Pressure Reducing Units” for company use. The specification defines in particular:

- the functional, safety and construction requirements that pressure regulators for supplying end-users must meet in order to be approved for company use and to be installed on gas distribution networks;

- the type of system in relation to capacity, pressure and type of end-user;

- the methods of approval of PRUs for company use and the suitability tests.

## Field of application

This Technical Specification applies, in the case of direct purchase by Italgas Reti, whenever a new PRU covered by this specification must be approved for company use, produced by a new potential Supplier or by an existing Supplier.

# Specifications

- These technical specifications must be understood as an integral part of the "ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS."

- This specification contains the minimum technical requirements demanded by Italgas Reti based on the reference Legislative and Technical Standards.

- It is the Supplier's responsibility to ensure that the products supplied fully comply with the provisions of this technical specification and the applicable standards.

- If the materials in question are supplied by an installer, the installer must document their compliance.

- It is the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. sharp edges or incorrect directions for use and maintenance), which may jeopardise the health and safety of the Client's workers in relation to the provisions of Italian Legislative Decree no. 81/08, as amended and supplemented.

- For any technical and operational aspects that conflict with or are not mentioned in this technical specification but that nevertheless pertain to the design, installation, maintenance and use of the products themselves, it is the Supplier's responsibility to refer to the regulations in force.

- Compliance of the PRUs with this Specification, with the applicable fire safety regulations and legal requirements for safety and environmental protection are essential basic requirements for the supply of PRUs.

# Technical characteristics

PRUs must be constructed in accordance with the reference standards mentioned in paragraph 11, taking into account the requirements on the relevant parts of these standards in paragraph 9.

This specification is based on the following considerations:

- The PRU is not subject to significant stresses other than those caused by gas pressure;

- The PRU is located in places where the weather conditions may range:

    - temperature -10 ÷ +60 °C

    - humidity up to 95%.

Under these conditions, all the PRU elements must operate smoothly.

## Constituent elements and construction characteristics of PRUs

a)	The PRU 10, 25, 50 and the 70 Sm3/h "compact" model consists of a cabinet with connections to the conveying pipes. The cabinet contains within it both the mechanism constituting the gas pressure regulator and the required filter and safety devices. The PRU is designed to supply both a single end-user or several end-users and is installed on site by means of special joints shown in Appendix 1, Appendix 2 and Appendix 3.

b) The frame-mounted PRU 70 Sm3/h includes specially constructed "piping" for the installation of the end-user regulator with two safety devices of the total closure type for increasing downstream pressure (blocking). Each regulator model + locking device, must have the maximum overall dimensions shown in the diagrams of Appendix 3/ , Appendix 3/ , Appendix 3/  and is indicated as part "A".

The regulators approved for company use are interchangeable by installing the regulator + the two locking devices between two coupling flanges interposed downstream of the filter and upstream of the outlet valve of the unit. The frame which the PRU is installed on must be predisposed for the installation of a by-pass with threaded joint connections, inlet ND ¾" and outlet ND 1½" which can be used during maintenance work to maintain continuity of service. The overall dimensions of the "piping" on the frame are shown in the diagram in Appendix 3/ .

The maximum overall dimensions of PRUs provided for by this Technical Specification and approved for company use are shown in the relevant Appendices listed in paragraph 12.

### Filtration system

For PRUs 10, 25, 50 and 70 Sm3/h, constituted as shown in point 4 paragraph a), the filter must be incorporated in the regulator. It must have a filtering surface area suitable for ensuring the smooth operation of the regulator and a filtering capacity to ensure that solid particles with a size of  300 microns are stopped.

For the 70 Sm3/h frame-mounted PRU, the filter consists of a cylindrical casing with a horizontal axis, made of steel or aluminium alloy; minimum mechanical strength class: PN 6, flange angle connections; easily removable filter element with sufficient filtering capacity to guarantee the smooth operation of the regulator and ensure that solid particles with a size of  300 microns are stopped.

For further information on cartridge filters, see also Technical Specification 9991300 - "Cartridge filter elements for gas reduction and metering unit and plant filters.

### Pressure regulator

Its function is to reduce and regulate the outlet pressure under normal operating conditions. It consists of a self-activated device with the following construction features:

- diaphragm-type with spring-loaded contrast, (the diaphragm and seals must be made of materials resistant to the corrosive action of the elements and impurities contained in the gas and to stresses caused by gas pressure);

- body and covers: steel or non-ferrous metal materials; they must withstand a pressure of 7.5 bar for the upstream part, subject to MOP 5 bar and 2.5 bar for the downstream part;

- attachments for compact, angle PRUs 10, 25, 50 and 70 Sm3/h:

  - inlet, sphero-conical seat NF E 29-536 with UNI EN ISO 228/1 female threaded moving nut,

    - ND ¾" for PRUs 10, 25, 50 Sm3/h;

    - ND 1" for compact PRUs 70 Sm3/h;

  - outlet, flat-seated, with UNI EN ISO 228/1 female threaded moving nut,

    - ND 1 ¼” for PRUs ≤ 25 Sm3/h;

    - ND 1 ½” for compact PRUs from 50 Sm3/h and 70 Sm3/h;

- connections for 70 Sm3/h frame-mounted PRUs:

  - in-line, with threaded sleeve in accordance with UNI EN 10226-1.

### Pipes, joints and special parts comprising the 70 Sm3/h frame-mounted PRU:

The pipes, with related fittings, special parts and component materials, must comply with the requirements set out in the Ministerial Decree of 16 April 2008 and comply with the following specifications:

- S.T.V.F.C. 15AA300 “Welded steel pipes for methane pipelines”

- S.T.V.F.C. 17AA300 “Steel fittings”

They must also be suitable for the intended use in accordance with the regulations in force.

The materials must be suitable for the intended use and are described in Appendix 3/  in Table 5.

The pipes, with related fittings and special parts, must be made of steel and subjected to a suitable surface painting with two coats of grey anti-rust paint on a prepared base,

### Frame joints for 70 Sm3/h PRUs

The connecting joints of the pipes with each other, with the related fittings and with the equipment constituting the PRU must be designed and manufactured in such a way as to guarantee a perfect seal over time, even in the presence of vibrations and/or mechanical stresses to which the system elements may be subjected.

The number of threaded joints (which may never be used for pipes with ND ≥ 50) must be kept to a minimum in order to reduce the possibility of gas leaks from the system. These joints must comply with UNI EN 10226.

In order to ensure a better seal, it is permissible to alternatively apply on the ends of the same:

- hemp with suitable, long-lasting glues;

- polytetrafluoroethylene tape or other equivalent materials specifically declared suitable according to UNI EN 751-3.

Welded connections must comply with current standards and qualified procedures.

Flange joints must comply with applicable laws, directives and standards, taking into account the technical/construction characteristics of the individual piece of equipment.

These characteristics, which must be adhered to when selecting flanges, are indicated, where present, in the various chapters of this Technical Specification.

## Functional characteristics

The PRU must fulfil the following functions:

- maintain the required regulation pressure at values compatible with the proper functioning of the installed end-user equipment;

- ensure continuity of the gas supply.

End-user reducers must meet the safety requirements indicated in UNI 8827, UNI 11655 and Ministerial Decree of 16 April 2008.

In particular, each PRU must perform the "REDUCTION" by means of a self-activated reducer-regulator consisting of a single or dual regulation stage with spring command for Q = 10, 25, 50 and 70 Sm3/h.

The following Table 1 shows the "MINIMUM FLOW RATE" (Qmin) values at minimum upstream pressure (OPumin) that the PRUs must guarantee depending on the size and required accuracy class indicated in point 4.2.4.

- Table 1

| ITALGAS RETI material code | PRU | MINIMUM FLOW RATE (Qmin) |  |
| --- | --- | --- | --- |
|  |  | OPumin 0.1 bar | OPumin 0.5 bar |
| 40802321115 | 10 Sm3/h | 6 Sm3/h | 10 Sm3/h |
| 40802321117 | 25 Sm3/h | 10 Sm3/h | 25 Sm3/h |
| 40802321121 | 50 Sm3/h | 16 Sm3/h | 50 Sm3/h |
| 40802321123 | 70 Sm3/h (compact) | 20 Sm3/h | 70 Sm3/h |
| 48001779314 | 70 Sm3/h (on frame) | 25 Sm3/h | 70 Sm3/h |

Table 2 highlights the "MAXIMUM FLOW RATE" (Qmax) values that the PRUs must guarantee. The Qmax must correspond to 150% of the minimum flow rate specified in Table 1.

- Table 2

| ITALGAS RETI material code | PRU | MAXIMUM FLOW RATE (Qmax) |  |
| --- | --- | --- | --- |
|  |  | OPumin 0.1 bar | OPumin 0.5 bar |
| 40802321115 | 10 Sm3/h | 9 Sm3/h | 15 Sm3/h |
| 40802321117 | 25 Sm3/h | 15 Sm3/h | 37 Sm3/h |
| 40802321121 | 50 Sm3/h | 24 Sm3/h | 75 Sm3/h |
| 40802321123 | 70 Sm3/h (compact) | 30 Sm3/h | 105 Sm3/h |
| 48001779314 | 70 Sm3/h (on frame) | 37 Sm3/h | 105 Sm3/h |

### Maximum operating pressure (MOPu)

Maximum upstream operating pressure (MOPu): 0.5 MPa (5 bar).

### Regulated pressure downstream of the first stage (where applicable)

Must be:

- 0.15 bar for MOP ≤ 1.5 bar

- 0.5 bar for MOP >1.5 bar

### Required regulation pressure OPd

22 mbar  10%. The pressure regulation setting must be calibrated and certified by the PRU Manufacturer.

### Accuracy class

- PRU 10, 25, 50 and 70 Sm3/h compact model:  10% of regulated pressure calibration value in the range 5100% of the flow rate delivered at upstream pressures OPu 0.5  5 bar;

- 70 Sm3/h frame-mounted PRU:  5% in the range 10 100% of the flow rate delivered at upstream pressures OPu 0.5  5 bar.

### Closing overpressure

- PRU 10, 25, 50 and 70 Sm3/h compact model:  135% of regulated pressure;

- 70 Sm3/h frame-mounted PRU:  120% of regulated pressure;

### Device for discharge into the atmosphere

This must be incorporated in the regulator and the calibration must be carried out and certified by the Manufacturer; the overflow rate must be < 400 L/h. The overflow device must trip at the following pressure:

  - PRU 10, 25, 50 and 70 Sm3/h compact model: 32.5 mbar  10%;

  - 70 Sm3/h frame-mounted PRU: 30 mbar   10%;

### Safety device

The 10, 25, 50 and 70 Sm3/h reducer-regulators must be equipped with the following safety devices:

#### Dual regulation stage (where applicable)

#### Manual-reset locking device for maximum regulated downstream pressure

- Pressostatic control;

- Own seat and obturators;

- Calibration carried out and certified by the Manufacturer:

  - PRU 10, 25, 50 and 70 Sm3/h compact model: 40 mbar  10%;

  - 70 Sm3/h frame-mounted PRU: 38 mbar  2 mbar.

#### Manual-reset locking device for minimum regulated downstream pressure

- PRU 10, 25, 50 and 70 Sm3/h compact model: must trip to prevent the downstream pressure from dropping below 10 mbar;

- frame-mounted PRU 70 Sm3/h: must trip to prevent the downstream pressure from dropping below 10 mbar.

## Technical assessment

In relation to Legislative Decree 81/08, as amended and supplemented, Italgas Reti reserves the right, in its evaluation of the use of the proposed products, to consider the operational consequences deriving from the conditions of use of the equipment as prescribed by the Supplier in the "Use and Maintenance Manual".

# Abatement of ACOUSTIC emissions

In relation to the need to install the PRU in compliance with the legal provisions in force, regarding noise pollution of the environment (acoustic emissions), they must comply – by means of the expedients deemed most suitable by the Supplier – with the following emission limit value expressed as a continuous equivalent weighted sound pressure level "A" (Leq A), under conditions of maximum output:

- Table 3

Emission limit value of PRU under standard conditions – Leq in dB(A)

Microphone placed 1.20 m  1.50 m above the ground and at a distance of 1 m from the cabinet walls

dB(A)  65

Although the above is not the standard solution, Italgas Reti may specifically request, with a separate quotation to be indicated in the offer phase, the supply of plants meeting more stringent noise emission levels, depending on the requirements imposed by current legislation.

# Marking

Each regulator must be provided with an irremovable identification plate on which the following information must be stated:

- Manufacturer's references (name and/or logo and/or registered trademark);

- Manufacturing site;

- Regulator model (PCD);

- PCD Serial no.;

- Year of construction;

- Size and type of connections;

- MOPu;

- MOPd;

- Nominal flow rate Qnom

- Maximum flow rate Qmax

- Allowed pressure (AP);

- Specific regulation range (Wds) and calibration pressure W(dsu);

- Specific calibration range (Wdsc/Wdsu) of the block valve (if any) and its calibration Pdso/Pdsu;

- Operating temperature range (Class 2 – standard UNI EN 334);

- Diameter of the valve seat or internal parts of the valve*;

- Seal class according to UNI EN 1349, if applicable;

- The direction of flow is clearly and permanently marked on the regulator body with an arrow.

* = only in case different sizes of the same regulator series are supplied.

# TYPE TEST

During the design phase of the PRU, it will be the Supplier's responsibility to carry out at recognised laboratories or directly at the Supplier's premises all the "Type Tests" envisaged by the reference standards and/or the Supplier's own design standards and the standards referred to therein to verify the intended end use of the PRU.

Note:

Type tests are not envisaged in the event that Italgas Reti deems that any modifications made by the Supplier to the PRUs already accepted for company use, affecting the structure and/or the arrangement of the piping connecting the equipment, do not affect the functionality, safety and reliability of the PRU.

# DOCUMENTATION required from the supplier

## Supplier

- The potential Supplier must be qualified as an ITALGAS Supplier.

## Documentation for the company approval process

### New Supplier

- The potential Supplier must:

- 1) Submit the documentation listed under 8.2.1.1. or 8.2.1.2. in connection with the proposed product to the "SERTEC-NORM" Department for technical evaluation.

#### Standardised products

- "Declaration of Conformity" in accordance with the UNI CEI EN ISO/IEC 17050-1 standard (see example shown in Appendix 4 of this Technical Specification) relating to:

- this Technical Specification; ,

- the ITALGAS RETI company documents (Material Tables) cited in this Technical Specification,

- any further specific documents (legislative provisions, applied standards, etc.) to which the Supplier refers for the design and construction of its products.

- List of references of the main customers using the proposed materials.

- 3)	Documentation reporting the results and methods of execution of laboratory and/or field tests as required in ITALGAS RETI documents or, when not specified, according to any specific reference standards.

- 4)	Any product and/or process certifications issued by officially recognised bodies;

- 5)	Whatever else the potential Supplier considers useful to better qualify the product.

If, on the basis of the design of a product intended for use in potentially explosive atmospheres (Directive 2014/34/EU), the Supplier determines that its product does not fall within the scope of the aforementioned Directive, the Supplier must submit a declaration of assumption of responsibility (see the example in Appendix 5 of this Technical Specification) which certifies that, following the risk analysis carried out, the product does not have any potential ignition sources of its own, and therefore does not fall within the scope of Legislative Decree no. 85/2016 (Directive 2014/34/EU) and can therefore be installed in all the zone types referred to in Legislative Decree no. 233/03 (Directive 1999/92/EC).

Based on the design of a product intended for use under pressure (Legislative Decree no. 93/2000 as amended and supplemented by Directive 2014/68/EU), the Supplier must in any case provide at least a declaration of compliance with Article 3, subsection 3 of the aforementioned Decree (see the example in Appendix 6 of this Technical Specification), certifying that the product is exempt from the requirements of such subsection.

#### Products being standardised

  - "Declaration of Conformity" in accordance with the UNI CEI EN ISO/IEC 17050-1 standard (see example in Appendix 4 of this Technical Specification) relating to:

- this Technical Specification,

- the ITALGAS RETI company documents (Material Tables) cited in this Technical Specification,

- any specific documents (legislative provisions, applied standards, etc.) to which the Supplier refers for the design and construction of its products.

- List of references of the main customers using the proposed materials.

- Documentation showing the results and method of execution of the tests described in point 9 carried out by the Supplier.

- Any product and/or process certifications issued by officially recognised bodies;

- Whatever else the potential Supplier considers useful to better qualify the product.

- Any other specific technical documentation agreed with ITALGAS RETI.

If, on the basis of the design of a product intended for use in potentially explosive atmospheres (Directive 2014/34/EU), the Supplier determines that its product does not fall within the scope of the aforementioned Directive, the Supplier must submit a declaration of assumption of responsibility (see the example in Appendix 5 of this Technical Specification) which certifies that, following the risk analysis carried out, the product does not have any potential ignition sources of its own, and therefore does not fall within the scope of Legislative Decree no. 85/2016 (Directive 2014/34/EU) and can therefore be installed in all the zone types referred to in Legislative Decree no. 233/03 (Directive 1999/92/EC).

If, on the basis of the design of a project intended for use under pressure (Legislative Decree no. 93/2000 as amended by EU Directive 68/2014), the Supplier determines that its product does not have the characteristics defined by the aforementioned Directive, it must in any case submit a declaration of inclusion in Article 3, subsection 3 of the aforementioned Directive, certifying the exemption of the product in compliance with the provisions of such subsection (see the example in Appendix 6 to this Technical Specification).

### Supplier with product already approved for company use

- If the Supplier is informed by ITALGAS RETI of the update of one or more reference documents for the supply of its products, it must send the "SERTEC-NORM" Department the documentation listed in point 8.2.2.1 or 8.2.2.2 in relation to the product already supplied.

#### Standardised products

"Declaration of Conformity” as required by the UNI CEI EN ISO/IEC 17050-1 standard (see example in Appendix 4 of this Technical Specification) relating to:

- this Technical Specification;

- the ITALGAS RETI company documents (Material Tables) cited in this Technical Specification,

- any further specific documents (legislative provisions, applied standards, etc.) to which the Supplier refers for the design and construction of its products.

For serial products, should the Supplier wish to supplement the offer, it must follow the provisions in point 8.2.1.1.

For ITALGAS RETI standardised products, should the Supplier wish to make modifications that do not comply with the reference documents, it must follow the requirements of point 8.2.1.2.

#### Products being standardised

As described in point 8.2.1.2

Products undergoing standardisation may be subjected to laboratory and/or field tests in agreement with ITALGAS RETI's Technical Department.

## Test Documentation

The Supplier must issue a “type 3.1” Inspection and Material Certificate in accordance with UNI EN 10204, stating that the PRUs supplied are compliant with the requirements of these specifications as well as the legislative provisions as per point 11.

For 703/h frame-mounted PRUs, the Supplier must also produce a test report for each of the tests containing at least the following information:

- Name of the authorised person responsible for the test;

- Test date;

- System manufacturer;

- Identification of the section to which the test relates;

- Design pressure;

- Pressure reached during the test and the period of time for which it was maintained;

- Test fluid;

- Test results;

- Reference to the test procedure (if any);

- Instrumentation used for the test with indication of calibration validity;

- Type and serial number of the instrument used for the test.

Registration of the full production/test documentation completed by the Supplier must be kept (on the basis of legal provisions) for 10 years under its responsibility, and must be made available whenever requested by the Client.

## Supply Documentation

- Documents compliant with Legislative Decree no. 286 of 21 November 2005, as amended.

In addition, for each individual PRU, upon delivery the Supplier must provide to the DESTINATION UNIT  a technical file (Data Book) containing at least the following documentation:

- “Type 3.1” Inspection and Material Certificates in accordance with UNI EN 10204;

- Use and maintenance booklet in Italian, containing information on the safe use of connections and instructions and safety requirements regarding commissioning and decommissioning;

- Functional diagram, construction drawing and equipment list with materials used (for 703/h frame-mounted PRUs);

- Recommended spare parts list of equipment subject to preventive maintenance;

- Storage requirements for the PCD and any spare parts;

- Declaration of conformity and compliance with applicable UNI standards (e.g. UNI 8827, UNI 11655);

- Declaration of conformity with applicable legislation;

- Declaration of conformity of installed equipment with applicable directives;

- Test report (for 70 Sm3/h frame-mounted PRUs);

- For equipment covered by the PED Directive 2014/68/EU (e.g. filters), for which at least two of the following conditions arise:

    - Internal diameter in mm or nominal dimensions 500 or less;

    - Maximum allowed pressure AP 6 bar or less;

    - The product of the internal diameter in mm or nominal dimensions ND times the maximum allowed pressure 3000 or less,

the Supplier must make available the documentation containing the basic data and construction characteristics (e.g. thicknesses) required to carry out integrity checks of the various components (external equipment body, ellipsoidal caps, etc.) of the pressure equipment.

## Final Documentation

### Procedure successfully completed

The Supplier receives from ITALGAS RETI notice of approval for company use.

### Procedure failed

The Supplier receives from ITALGAS RETI notice of a negative outcome.

# TESTS AND INSPECTIONS

Italgas Reti reserves the right:

- To be present with its own Inspectors and/or Inspection Companies appointed by the same to carry out tests/checks c/o your plant and at your care and expense, to check the constructive and functional compliance of the materials in accordance with the specifications and/or reference standards.

- To verify, upon receipt and/or under actual conditions of use, the perfect compliance of the goods with the functional technical characteristics expressly indicated in the Contract.

It remains understood that the favourable outcome of our Inspection and checking of the materials shall not release you in any way from your responsibilities and obligations arising from every individual Contract.

The tests and inspections described below must be carried out by the Supplier:

- Visual inspections and dimensional checks (point 9.1):

- of each individual PRU in the case of 10, 25, 50 and 70 Sm3/h compact PRUs;

- of the entire unit and individual components (regulator, blocking device, valves, etc.) in the case of the 70 Sm3//h frame-mounted PRUs.

- In the case of 70 Sm3//h frame-mounted PRUs:

- Mechanical strength test (point 9.2);

- Pneumatic external leak test (point 9.3);

- Non-destructive testing of welds (point 9.4).

- Functional testing of the individual regulators (to be carried out in accordance with the requirements of UNI EN 334) and appliances and/or the fully assembled unit with regard to:

- maximum flow rates and pressure drops;

- precision and stability of regulation over the entire range of flow rates and pressures;

- repeated tripping tests of safety devices or anything else deemed important to ensure the correct and reliable operation of the system.

The tests must be certified in accordance with UNI EN 10204 type 3.1.

## Visual and dimensional inspection

The construction and dimensional conformity with the construction drawing must be checked.

The dimensional tolerances of the threads must be those specified in the relevant standards.

The inspections must be certified in accordance with UNI EN 10204 type 3.1.

## Mechanical strength test for 70 Sm3/h frame-mounted PRUs

A mechanical strength test must be carried out in the factory and recorded. Test procedures must be chosen according to UNI EN 12327.

The mechanical strength test must have a minimum duration of 4 hours, after temperature stabilisation, and must be performed under the conditions specified below in Table 4:

- Table 4

| Test pressure Pcol | MOP |
| --- | --- |
| 2.5 bar | MOP ≤ 1.5 bar (part affected by downstream pressure) |
| 7.5 bar | 1.5 < MOP ≤ 5 bar (part affected by upstream pressure) |

The test can be performed by means of a hydraulic test or by using air or inert gases.

The mechanical strength test is not required for:

- Pressure reducer-regulator, blocking device, filter

for which the factory test must be carried out in accordance with the relevant regulations in force and in any case with a test pressure not lower than the values indicated in Table 4.

If the Supplier can prove by means of suitable existing documentation that the components of the 70 Sm3/h frame-mounted PRU have been previously tested at least to the required test pressure, the strength test need not be repeated on these components.

## Pneumatic external leak test for 70 Sm3/h frame-mounted PRUs

After the strength test, all the components that were removed from the installation before the test must be reinstalled.

The entire installation must be subjected to an external pneumatic leak test. The test must have a minimum duration of 30 minutes, after temperature stabilisation, and must be carried out under the following conditions:

- Upstream section: maximum operating pressure;

- Downstream section: 0.10 bar.

Air or inert gas or mains gas must be used as the test fluid.

The perfect tightness of the pressure reducer-regulator obturators and safety devices must also be checked and guaranteed by means of a pneumatic leak test, to be carried out for one minute immediately after the obturator has closed.

## Inspection of welded joints on 70 Sm3/h frame-mounted PRUs

Welding of steel pipes must be carried out in accordance with UNI EN 12732, according to qualified procedures complying with UNI EN ISO 15614-1 or equivalent standards.

Welders must be qualified in compliance with UNI EN ISO 9606-1 or equivalent standards.

The Supplier must carry out non-destructive testing of the welds of the PRUs at its own expense, in accordance with the relevant standards.

All non-destructive testing operations must be carried out by qualified Level 2 personnel in accordance with formalised procedures. Level 2 personnel must be certified in compliance with UNI EN ISO 9712.

The non-destructive testing (NDT) to be carried out on welded joints subjected to pressure must include at least the following checks:

- Head-to-head welds must be radiographed at 20% in accordance with Italgas Reti and in compliance with UNI EN 17636-1 (Class B); the acceptability level is level 1 according to UNI EN 10675-1.

- Any welds that cannot be radiographed must be checked 100% with liquid penetrants in accordance with UNI EN ISO 3452-1, acceptability level 1 to UNI EN ISO 23277 or with magnetic particles in accordance with UNI EN ISO 17638, acceptability level 1 according to UNI EN ISO 23278.

As regards the quality of the welded joints, Italgas Reti reserves the right, at any time and without prior notice, to have its own "inspectors" carry out an inspection of the welded joints, in quantities not exceeding 10% of the total number of joints welded during assembly, with non-destructive testing (e.g. radiographic tests). The results of any tests already carried out by the Supplier are accepted provided that the joints indicated by Italgas Reti coincide with those subjected to the tests.

## Right of the client

It is Italgas Reti's right, for each purchase order, to request from the Supplier:

- further technical and/or graphic documentation,

- additional laboratory and/or field tests,

in order to verify the conformity of the proposed products with this technical specification and the cited standards to which reference is made.

# CONDITIONS OF SUPPLY

Supplier's Standard in compliance with Legislative Decree no. 152 of 3 April 2006 as amended and supplemented.

# REFERENCE STANDARDS

- Law no. 447/95 – Framework Law on Noise Pollution, as amended.

- Legislative Decree no. 85 of 19 May 2016 – "Implementation of Directive 2014/34/EU on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres".

- Legislative Decree no. 233 of 12 June 2003 – "Implementation of Directive 1999/92/EC on minimum requirements for improving the safety and health protection of workers exposed to the risk of explosive atmospheres".

- Legislative Decree no. 93 of 25 February 2000, as amended. - "Implementation of Directive 97/23/EC on pressure equipment and Directive 2014/68/EU on the harmonisation of the laws of the Member States relating to the making available on the market of pressure equipment (recast), providing for its repeal".

- Legislative Decree No. 81 of 9 April 2008 as subsequently amended and supplemented. “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”.

- Legislative Decree No. 152 of 3 April 2006 as subsequently amended and supplemented. “Environmental standards”.

- Legislative Decree No. 286 of 21 November 2005 as subsequently amended and supplemented. “Provisions for the regulatory reorganisation of the regulated liberalisation of the road haulage business”.

- Ministerial Decree of 16 April 2008 “Technical regulations for the design, construction, testing, operation and supervision of works and distribution systems and direct lines for natural gas with a density not exceeding 0.8”;

- UNI 8827: "Gas pressure control systems operating with upstream pressure between 0.04 bar and 5 bar - Design, construction and testing".

- UNI 11655: "Pressure Control Devices (PCDs) - Design, manufacturing and testing".

- UNI EN 334: "Gas pressure regulators for inlet pressures up to 100 bar."

- UNI EN 12327 "Gas infrastructures - Pressure testing, commissioning and decommissioning procedures for gas supply networks - Functional requirements".

- UNI EN 12732 "Gas infrastructures - Welding of steel pipework - Functional requirements".

- UNI EN 751-3: "Sealing material for metallic threaded joints in contact with 1st, 2nd and 3rd family gases and hot water - Unsintered PTFE tapes".

- UNI EN 682 "Elastomeric seals - Materials requirements for seals used in pipes and fittings carrying gas and hydrocarbon fluids".

- UNI EN 1349 "Industrial process control valves".

- UNI EN 10702-1: "Gas pressure regulating installations or metering systems operating with upstream pressure between 0.04 bar and 12 bar - Part 1: Pressure control surveillance  ".

- UNI EN ISO 10226-1: “Pipe threads for thread seal coupling. Tapered External and Parallel Internal Threads  Dimensions, Tolerances and Designation”.

- UNI EN ISO 228-1: “Pipe threads for non-thread seal coupling. Dimensions, Tolerances and Designation”.

- UNI EN ISO 15614-1 “Specification and qualification of welding procedures for metallic materials - Welding procedure test - Part 1: Arc and gas welding of steels and arc welding of nickel and nickel alloys”.

- UNI EN ISO 9606-1 “Qualification testing of welders - Fusion welding - Part 1: Steels”.

- UNI EN ISO 9712 "Non-destructive testing - Qualification and certification of non-destructive testing personnel - General principles".

- UNI EN ISO 17636-1 "Non-destructive testing of welds - Radiographic testing - Part 1: X and gamma-ray techniques with film".

- UNI EN ISO 10675-1 "Non-destructive testing of welds - Part 1: Radiographic testing of butt welds of steel, nickel, titanium and their alloys - Acceptance levels".

- UNI EN ISO 3452-1 "Non-destructive testing - Penetrant testing - Part 1: General Principles”.

- UNI EN ISO 23277 "Non-destructive testing of welds - Penetrant testing - Acceptance levels".

- UNI EN ISO 17638 "Non-destructive testing of welds - Magnetic particle testing".

- UNI EN ISO 23278 "Non-destructive testing of welds - Magnetic particle testing - Acceptance levels".

- UNI EN ISO 3183: "Steel pipe for pipeline transportation systems”.

- UNI CEI EN ISO/IEC 17050 - "Conformity assessment - Supplier's declaration of conformity”.

- ASME B16.5 “Pipe Flanges and Flanged Fittings NPS 1/2 Through NPS 24 Metric/Inch Standard”.

# APPENDICES

- Appendix 1: Maximum overall dimensions of the PRU ≤ 25 Sm3/h

- Appendix 2: Maximum overall dimensions of the PRU of 50 Sm3/h

- Appendix 3: Maximum overall dimensions of the PRU of 70 Sm3/h

- Appendix 3/a: Overall dimensions of the 70 Sm3/h frame

- Appendix 3/b: Overall dimensions of the FIORENTINI model PRU of 70 Sm3/h

- Appendix 3/c: Overall dimensions of the TARTARINI model PRU of 70 Sm3/h

- Appendix 3/d: Overall dimensions of the REGAS model PRU 70 of Sm3/h

- Appendix 3/e: Filter for end-user MPB reduction unit with Q ≤ 70 Sm3/h for frame-mounting

- Appendix 4: “Sample declaration of conformity with this technical specification”

- Appendix 5: “Sample declaration of exclusion from Directive 2014/34/EU”

- Appendix 6: “Sample declaration of SOUND ENGINEERING PRACTICE (SEP)”

# annexes

- Annex 1: S.T.V.F.C. 9991300 - "Cartridge filter elements for filters of gas reduction and metering units and plants".

- Annex 2 – S.T.V.F.C. 15AA300: “Welded steel pipes for natural gas pipelines”.

- Annex 3 – S.T.V.F.C. 17AA300 “Steel fittings”.

- Annex 4 – S.T.V.F.C. 2000300 “Steel valves for gas pipelines”.

## Appendix 1

Maximum overall dimensions of the PRU  25 Sm3/h

Italgas Reti material code: 10 Sm3/h : 40802321115

Italgas Reti material code: 25 Sm3/h : 40802321117

## Appendix 2

Maximum overall dimensions of the PRU  50 Sm3/h

Italgas Reti material code 50Sm3/h : 40802321121

## Appendix 3

Maximum overall dimensions of the compact PRU = 70 Sm3/h

Italgas Reti material code 70Sm3/h : 40802321123

## Appendix 3/

Overall dimensions of the frame 70 Sm3/h

Frame material code for end-user 70 Sm3/h: 48001779314

## Appendix 3/

Frame component materials for PRU of 70 Sm3/h

(see references on diagram in APPENDIX 3/a)

- Table 5

| Pos. | DESCRIPTION | Table |
| --- | --- | --- |
| 1 | Steel pipe for methane pipelines, smooth ends, unfinished - OP ≤ 1.2 MPa (12 bar), ND 3/4" | G. 151-2…. |
| 2 | Stiffening bracket | - |
| 3 | Floating ball steel valve, butt-weld end, ANSI 150, ND ¾ | G. 20/A…. |
| 4 | Normal sleeve, medium series, ND ¾" | M. 17867.. |
| 5 | Plug with rounded edge T9 (ex Plug FIG. 290), ND ¾” | G. 176…. |
| 6 | Steelflange* to be butt-welded, complying with ANSI B 16.5 class 150, ND ¾" | - |
| 7 | Filter for MPB end-user reduction units with Q £ 70 st m³/h (see APPENDIX 3/e) | - |
| 8 | Steel flange* to be butt-welded, ANSI 150 R.F. ND 1" ½ | M. 174960/1. |
| 9 | Steel overlap flange, complying with ANSI B 16.5 class 150, ND 1" ½ | - |
| 10 | Threaded steel pipe section with one smooth end to be welded, ND 1" ½ | M. 178640/1. |
| 11 | Normal sleeve, medium series, ND ½" | M. 17867.. |
| 12 | Plug with rounded edge T9 (ex Plug FIG. 290), of malleable cast iron, galvanised, ND ½" | G. 176…. |
| 13 | Reduced bore ball valve, brass, threaded ends, lightweight, with cap, ND 1" ½ | G. 2061… |
| 14 | Threaded steel pipe section with one smooth end to be welded, ND 1" ½, and Steel pipe for methane pipelines, with smooth ends, unfinished - OP ≤ 1.2 MPa (12 bar), ND 1" ½ | M. 178640/1. G. 151-2…. |
| 15 | Steel tee for butt-welding for LP and MP gas installations ND 1" ½ | G. 177/A… |
| 16 | Steel 90° elbow (TYPE 3 D) R = 1.5 ND (formerly 90° Bend - R = 1.5 ND) for butt-welding, for BP and MP gas installations, ND 1" ½ | G. 177/A… |
| 17 | Steel pipe for methane pipelines, smooth ends, unfinished - OP ≤ 1.2 MPa (12 bar), ND 1" ½ | G. 151-2…. |
| 18 | Plug with rounded edge T9 (ex Plug FIG. 290), of malleable cast iron, galvanised, ND 1"½ | G. 176…. |

* : The flange can be omitted by directly welding the steel pipe, at the inlet, to the filter body

## Appendix 3/

Overall dimensions PRU model FIORENTINI 70 Sm3/h (detail A of the frame)

Italgas Reti material code: 48001779315

Table 6

| Pos. | DESCRIPTION | Table |
| --- | --- | --- |
| 1 | Synthetic seal according to UNI EN 682 | - |
| 2 | Steel overlap flange, complying with ANSI B 16.5 class 150, ND 1" ½ | - |
| 3 | Steel 90° elbow (TYPE 3 D) R = 1.5 ND (formerly 90° Bend - R = 1.5 ND) for butt-welding, for BP and MP gas installations, ND 1" ½ | G. 177/A… |
| 4 | Steel pipe for methane pipelines, smooth ends, unfinished - OP ≤ 1.2 MPa (12 bar), ND 1" ½ | G. 151-2…. |
| 5 | Take from "Concentric reducer EN 10253-2 - shape 2 - 48.3 x 2.6 x 33.7 x 2.6 - P235" | - |
| 6 | Pressure reducer regulator for MPB end-user with flow rate up to 70 st m3/h - Fiorentini Dival 512 | - |
| 7 | Threaded steel pipe section with one smooth end to be welded, ND 1" ½ | M. 178640/1. |

## Appendix 3/

Overall dimensions PRU model TARTARINI 70 Sm3/h (detail A of the frame)

Italgas Reti material code: 48001779315

- Table 7

| Pos. | DESCRIPTION | Table |
| --- | --- | --- |
| 1 | Synthetic seal according to UNI EN 682 | - |
| 2 | Steel overlap flange, complying with ANSI B 16.5 class 150, ND 1" ½ | - |
| 3 | Steel 90° elbow (TYPE 3 D) R = 1.5 ND (formerly 90° Bend - R = 1.5 ND) for butt-welding, for BP and MP gas installations, ND 1" ½ | G. 177/A… |
| 4 | Threaded steel pipe section with one smooth end to be welded, ND 1" ½ | M. 178640/1. |
| 5 | Pressure reducer regulator for MPB end-user with flow rate up to 70 st m3/h - Tartarini B249 | - |

## Appendix 3/

Overall dimensions PRU model REGAS 70 Sm3/h (detail A of the frame)

Italgas Reti material code: 48001779315

- Table 8

| Pos. | DESCRIPTION | Table |
| --- | --- | --- |
| 1 | Synthetic seal according to UNI EN 682 | - |
| 2 | Steel overlap flange, complying with ANSI B 16.5 class 150, ND 1" ½ | - |
| 3 | Steel 90° elbow (TYPE 3 D) R = 1.5 ND (formerly 90° Bend - R = 1.5 ND) for butt-welding, for BP and MP gas installations, ND 1" ½ | G. 177/A… |
| 4 | Steel pipe for methane pipelines, smooth ends, unfinished - OP ≤ 1.2 MPa (12 bar), ND 1" ½ | G. 151-2…. |
| 5 | Take from "Concentric reducer EN 10253-2 - shape 2 - 48.3 x 2.6 x 33.7 x 2.6 - P235" | - |
| 6 | Pressure reducer regulator for MPB end-user with flow rate up to 70 st m3/h - Regas RBI 2612 | - |
| 7 | Threaded steel section with one smooth end to be welded, ND 1" ½ | M. 178640/1. |

## Appendix 3/

Filter for end-user MPB reduction unit with Q ≤ 70 Sm3/h for frame-mounting

| Maximum operating pressure | 5 bar |
| --- | --- |
| Cylindrical body material | Steel UNI EN ISO 3183 Grade PSL1 or aluminium alloy |
| Ellipsoidal cap material | Steel Grade B ASTM A 234 WPB - σ = 240 N/mm2 |
| Material of inlet-outlet pipe | Steel UNI EN ISO 3183 Grade PSL1 |
| Coupling flange material | Steel ASTM A 105 |
| Blind closing flange material | Steel ASTM A 105 |
| Surface treatment | Painting with two coats of grey anti-rust paint on a prepared base |
| Marking | Manufacturer's name and logo, ND, PN, conformity to Directive 2009/142/EC |
| Filtration class |  300 microns |

## Appendix 4

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN ISO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

(4)	The following products manufactured by us:

| Our material code (5) | Italgas Reti material code (6) |
| --- | --- |
| xxx | xxx |
| xxx | xxx |

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(7)	S.T.V.F.C. 2321300	End-user pressure reducing units from road pipes	Edition 1 of 15/06/2017

With upstream pressure between 0.5 and 5

Additional information:

(8) 	...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(9) 	............................................................. 			......................................................................................................................

(Name and position) 					(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- The “subject” must be unambiguously described so that the declaration of conformity can be referred to the subject in question.

- List all the products for which company use authorisation is being requested.

- For each individual product supplied, state the material code used by the Supplier.

- For each individual product supplied, please quote the material code assigned by Italgas Reti, which can be found in the Italgas Reti reference documents. If there are none, please contact SERTEC-NORM.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

## Appendix 5

ATEX Exclusion Declaration

We ..............................................................................................................................................................

(name of organisation)

with registered office in .............................................................................................................

(address)

as the .................................................................................................................................................

(Manufacturer / Authorised Representative)

declare under our sole responsibility that the products series

.....................................................................................................................................................................

.....................................................................................................................................................................

(name, type or model, batch, group or serial numbers)

described in the Technical Specification / document(s)

.....................................................................................................................................................................

.....................................................................................................................................................................

(when necessary)

to which this declaration refers, comply with the following legislative / regulatory document(s)

.....................................................................................................................................................................

.....................................................................................................................................................................

(title(s) and/or number(s) and date(s) of publication of the standard(s) or other legislative and/or regulatory document(s))

and, according to Article 1, subsection 1a) of Directive 2014/34/EU of 26 February 2014 (Legislative Decree no. 85 of 19 May 2016) and Chapter 1 of ATEX 2014/34/EU GUIDELINES (first edition), based on an ATEX analysis (ref. paragraph 32 of the aforementioned ATEX 2014/34/EU GUIDELINES), do not fall within the scope of the Directive 2014/34/EU, as they do not risk causing an explosion due to the lack of potential ignition sources as defined in Standard UNI EN 1127-1, when used in systems that comply with the following legislative and/or regulatory documents

.....................................................................................................................................................................

.....................................................................................................................................................................

.....................................................................................................................................................................

(title and/or number and date of publication of legislative and/or regulatory documents)

They can therefore be installed in all types of zones as defined in Legislative Decree no. 81 of 9 April 2008, as amended, Title XI (Directive 1999/92/EC of 16 December 1999).

.................................................................. 		..................................................................................................................................

(place and date of issue)				(name and signature or equivalent stamp of authorised person)

## Appendix 6

Declaration of falling within Article 3, subsection 3 of Legislative Decree no. 93

(SEP Declaration)

We ..............................................................................................................................................................

(name of organisation)

with registered office in .............................................................................................................

(address)

as the .................................................................................................................................................

(Manufacturer / Authorised Representative)

declare that, following the analysis carried out in accordance with Legislative Decree no. 93 of 25 February 2000 as amended. (Directive 2014/68/EU), product series:

..................................................................................................................................................................... ..................................................................................................................................................................... (name, type or model, batch, group or serial number)

described in the document:

…………………..………..……………………………………………………………………………….

…………………..………..……………………………………………………………………………….

(title and/or number and date of publication of the Standard(s) or other regulatory document(s))

to which this declaration refers, fall under Article 3, subsection 3 of Legislative Decree no. 93 of 25 February 2000 as amended, and are therefore subject to the provisions thereof. Consequently the products mentioned are not subject to CE marking for the application of Legislative Decree no. 93 of 25 February 2000 as amended.

Supplier means the party responsible for the design and construction of the products or its legal representative as defined in Legislative Decree no. 206 of 6 September 2005 as amended and supplemented. - "Consumer code, pursuant to Article 7 of Law no. 229 of 29 July 2003."

DESTINATION UNIT means the OPERATIONAL UNIT receiving the PRU.

SOUND ENGINEERING PRACTICE