“TECHNICAL SPECIFICATION FOR EVALUATION, SUPPLY AND TESTING”

S.T.V.F.C. 9991302

Heat exchangers and replacement service on existing installations

| Compiled by | SERTEC-NORM | LORO, SILVIO |
| --- | --- | --- |
| Checked by | SERTEC-NORM | VARESE, ENRICO |
| Checked by | PROMA-MATMA | SCOTTO, ENRICO |
| Checked by | SERTEC-LAB | SALAT,I EUGENIO |
| Checked by | HSEQ | BOLZONI, GIANLUCA |
| Checked by | PROMA/CMMAT | FASSINO, SILVIO |
| Checked by | PROMA-CMLASI | ZAMBRINI, LUCA |
| Approved by | SERTEC | COMAZZI, MARCO |

SUMMARY

1	PRELIMINARY INFORMATION	5

1.1	Cancels and replaces	5

1.2	Reason for issue	5

1.3	Definitions	5

2	PURPOSE AND FIELD OF APPLICATION	5

2.1	Purpose	5

2.2	Field of application	5

3	SPECIFICATIONS	5

4	Technical characteristics	6

4.1	General characteristics and reference standards	6

4.1.1	Construction, maintenance, use	6

4.1.2	Use in potentially explosive atmosphere	6

4.1.3	Pressure equipment	7

4.1.4	Handling of heat exchangers	7

4.1.5	Design data and documentation of the DESTINATION UNIT ()	7

4.2	General technical characteristics	7

4.3	Technical characteristics of exchangers for replacement	9

4.4	Accessories	11

4.5	Protective coating (painting)	11

4.6	Machining tolerances	12

4.7	Technical assessment	12

5	Marking	12

6	Type Test	13

7	DOCUMENTATION REQUIRED FROM THE SUPPLIER	13

7.1	Supplier()	13

7.2	Documentation for the company approval process	13

7.3	Test Documentation	14

7.4	Supply Documentation	14

8	TESTS AND INSPECTIONS	14

8.1	Dimensional inspection	15

8.2	Non-Destructive Testing (NDT)	15

8.3	Hydraulic testing	15

8.3.1	Tube bundle hydraulic testing	15

8.3.2	Shell hydraulic testing	15

8.4	Paint inspections	15

8.5	Right of the client	15

9	CONDITIONS OF SUPPLY	15

9.1	Packaging	16

10	REPLACEMENT SERVICE (On specific request)	16

10.1	DESIGN AND EXECUTION OF REPLACEMENT WORKS	16

10.2	MECHANICAL WORKS	16

10.3	CIVIL WORKS (where necessary)	17

10.4	DISPOSAL OF DECOMMISSIONED OR WASTE MATERIALS	17

10.5	GUIDELINES FOR DRAFTING/SUPPLEMENTING THE SAFETY PLAN	17

11	ReferenceStandards	17

12	APPENDICES	19

13	ATTACHMENTS	19

Appendix 1	20

Appendix 2	21

# PRELIMINARY INFORMATION

## Cancels and replaces

This specification cancels and replaces T.S. 9991302, Edition 1, dated 14 May 2012 – Heat exchangers and replacement service on existing installations.

## Reason for issue

Updating of S.T.V.F.C. 9991302 and its reissue was necessary due to:

- issuing of new national and European standards (CEI and UNI);

- New legislative context;

- updating of Supply and Testing Criteria;

## Definitions

For definitions of the technical terms used in this specification, please refer to the relevant regulations, a non-exhaustive list of which can be found in the chapter 11 "Reference standards".

# PURPOSE AND FIELD OF APPLICATION

## Purpose

This Specification defines the technical characteristics and execution of the works for the replacement of deteriorated "Heat Exchangers" on existing "Reduction Plants".

## Field of application

It applies whenever the need arises to purchase / replace a “heat exchanger” on existing “Reduction Plants” covered by this specification, produced by a new potential Supplier or by an existing one.

# SPECIFICATIONS

- These technical specifications must be understood as an integral part of the "ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS."

- This specification contains the minimum technical requirements demanded by Italgas Reti based on the reference Legislative and Technical Standards. Under no circumstances may their acceptance mean that the Supplier waives its full responsibility for all the stages necessary for the realisation of the works covered by the contract.

- It is the Supplier's responsibility to ensure that the products supplied fully comply with the provisions of this technical specification and the applicable standards.

- if the products in question are supplied by an installer, the installer must document their compliance as required under “Documentation required from the Supplier”.

- It is the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. shavings and other production waste, sharp edges or incorrect directions for use and maintenance), which may jeopardise the health and safety of the Client's workers in relation to the provisions of Italian Legislative Decree no. 81/08, as amended and supplemented. Any improvement of the proposed product may be evaluated at the Client's discretion during the tender process.

- For any technical and operational aspects that conflict with or are not mentioned in this technical specification but that nevertheless pertain to the design, installation, maintenance and use of the products themselves, it is the Supplier's responsibility to refer to the regulations in force.

# Technical characteristics

  - The drawings shown in this specification should be considered as a “standard model shown as an example”, except for the specified dimensions and technical characteristics, which should be considered as binding.

  - Italgas Reti material code: N.C.

## General characteristics and reference standards

- This Specification defines the technical characteristics of the heat exchangers taking into account that the fluid flowing through the products covered by this Specification is natural gas with characteristics as per Ministerial Decree of 19 February 2007, published in the Official Gazette no. 65 of 19.03.2007.

- Each "heat exchanger" described in this Specification must be:

  - manufactured, controlled and certified in accordance with the legal and technical standards stated in the following points;

  - accompanied by "Operating Instructions" in Italian as prescribed by the reference standards.

### Construction, maintenance, use

All the products described in this specification must comply with the requirements of the Ministerial Decree of 16 April 2008 and the relevant Technical Standards referred to therein.

### Use in potentially explosive atmosphere

Each “heat exchanger” must be able to be used without risk within potentially explosive atmospheres and therefore, with reference to Legislative Decree no. 233 of 12 June 2003, must comply with the provisions of Legislative Decree no. 85 of 19 May 2016 where applicable.

Compliance with this requirement must be demonstrated, if the product falls within the scope of Legislative Decree No. 85/16:

- By product "marking";

- By the documentation required, as appropriate, by the aforementioned Decree and by the relevant harmonised standards (e.g. "EU Declaration of Conformity" or "Certificate of conformity", "operating and maintenance instructions" in Italian, possible "Certificate of conformity" following EU type-examination).

Heat exchangers are installed in the reduction and metering plants operating in "zone 1".

The Manufacturer must carry out a risk analysis at its own responsibility.

### Pressure equipment

Each "Heat Exchanger" described in this specification is normally used in the construction and operation of pressure networks conveying natural gas or in pressure reduction systems operated with upstream OP > 5 bar. Consequently, each "heat exchanger" is regulated by Legislative Decree no. 26 of 15 February 2016 implementing the Integration Directive 2014/68/EU ()

### Handling of heat exchangers

In compliance with the legal provisions in force on the use and operation of equipment (see Title VI of Legislative Decree no. 81/08 as amended), it is the Supplier's responsibility to equip the “Heat exchangers” that require it, with fittings (e.g. eyebolts) to enable them to be handled by lifting means.

### Design data and documentation of the DESTINATION UNIT ()

- Basic technical data for the design and adaptation of the "Heat Exchanger" for the system covered by this Specification will be provided in the documentation below:

- Flow diagram and equipment specification of the existing plant;

- Photographic documentation;

- Assembly diagrams (if any).

## General technical characteristics

- Each "heat exchanger" must:

- Be built for vertical use;

- Have a removable tube bundle, removable and inspectable distributor for heat outputs > 100,000 kcal/h (116.3 kW);

- Have a distributor not necessarily detachable but inspectable for heat outputs ≤ 100,000 kcal/h (116.3 kW);

- Have the tube bundle and ellipsoidal cap plating made of steel suitable for the purpose.

- Figure 1 - "Heat exchanger"

## Technical characteristics of exchangers for replacement

- The following points describe the characteristics of newly designed "heat exchangers" that can also be used to replace existing ones.

- Figure 2 - Newly designed "Heat Exchanger"

Table 1 - Standardised type

| - DESIGN DATA | - TYPE 1 | - TYPE 2 | - TYPE 3 | - TYPE 4 | - TYPE 5 | - TYPE 6 | - TYPE 7 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - WATER FLOW |  |  |  |  |  |  |  |
| - Nominal pressure NP | - 6 | - 6 | - 6 | - 6 | - 6 | - 6 | - 6 |
| - Maximum operating pressure (MOPu) bar | - 5 | - 5 | - 5 | - 5 | - 5 | - 5 | - 5 |
| - Max. water flow speed m/sec | - ≤ 0.5 | - ≤ 0.5 | - ≤ 0.5 | - ≤ 0.5 | - ≤ 0.5 | - ≤ 0.5 | - ≤ 0.5 |
| - Water flow line flanges ND | - (1) | - (1) | - (1) | - (1) | - (1) | - (1) | - (1) |
| - Water flow line flanges NP | - 6 | - 6 | - 6 | - 6 | - 6 | - 6 | - 6 |
| - Thermal conductivity at 100 °C - kcal/m² h °C | - < 1 | - < 1 | - < 1 | - < 1 | - < 1 | - < 1 | - < 1 |
| - Heat output kcal/h | - 28,400 | - 53,000 | - 94,600 | - 110,000 | - 154,800 | - 200,000 | - 251,000 |
| - Heating capacity kW | - 33 | - 62 | - 110 | - 128 | - 180 | - 233 | - 292 |
| - HEAT EXCHANGER DIMENSIONS |  |  |  |  |  |  |  |
| - A mm | - (2) | - (2) | - (2) | - (2) | - (2) | - (2) | - (2) |
| - B mm | - (2) | - (2) | - (2) | - (2) | - (2) | - (2) | - (2) |
| - C mm | - (2) | - (2) | - (2) | - (2) | - (2) | - (2) | - (2) |
| - D mm | - (2) | - (2) | - (2) | - (2) | - (2) | - (2) | - (2) |
| - H mm | - (2) | - (2) | - (2) | - (2) | - (2) | - (2) | - (2) |
| - L mm | - (2) | - (2) | - (2) | - (2) | - (2) | - (2) | - (2) |

(1) "ND Water flow line flanges" to be defined after inspection in relation to the WRMP in which the "Heat Exchanger" is to be installed.

(2) "Dimensions" to be defined after inspection in relation to the WRMP in which the "Heat Exchanger" is to be installed.

| - DESIGN DATA | - TYPE 1 | - TYPE 2 | - TYPE 3 | - TYPE 4 | - TYPE 5 | - TYPE 6 | - TYPE 7 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - GAS FLOW - DESIGN FEATURES for WRMP with UPSTREAM OP of 75 bar |  |  |  |  |  |  |  |
| - Nominal pressure ANSI | - 600 | - 600 | - 600 | - 600 | - 600 | - 600 | - 600 |
| - Max. line flow rate (Qlin) stm³/h | - 1,850 | - 3,000 | - 6,150 | - 7,190 | - 10,100 | - 11,875 | - 14,375 |
| - Max operating pressure (MOPu) - bar | - 75 | - 75 | - 75 | - 75 | - 75 | - 75 | - 75 |
| - Lower limit of minimum pressure (PuminL) bar | - 12 | - 12 | - 12 | - 12 | - 12 | - 12 | - 12 |
| - Minimum pipe sizing pressure (PminP) bar | - 12 | - 12 | - 12 | - 12 | - 12 | - 12 | - 12 |
| - Inlet/outlet pressure drop bar | - ≤ 5% PminP | - ≤ 5% PminP | - ≤ 5% PminP | - ≤ 5% PminP | - ≤ 5% PminP | - ≤ 5% PminP | - ≤ 5% PminP |
| - Max. gas flow speed m/sec | - ≤ 30 | - ≤ 30 | - ≤ 30 | - ≤ 30 | - ≤ 30 | - ≤ 30 | - ≤ 30 |
| - Minimum/maximum permissible temperature (TS) °C | - -10 / +100 - (3) | - -10 / +100 - (3) | - -10 / +100 - (3) | - -10 / +100 - (3) | - -10 / +100 - (3) | - -10 / +100 - (3) | - -10 / +100 - (3) |
| - Reduction line ND | - (4) | - (4) | - (4) | - (4) | - (4) | - (4) | - (4) |
| - Gas flow line flanges ND | - (4) | - (4) | - (4) | - (4) | - (4) | - (4) | - (4) |
| - Gas flow line flanges ANSI | - 600 RF | - 600 RF | - 600 RF | - 600 RF | - 600 RF | - 600 RF | - 600 RF |

(3) The minimum design temperature of the "heat exchanger" must be verified prior to design (see standard UNI 9167: If the ambient temperature is less than -10 °C, the minimum design temperature may not be higher than the minimum ambient temperature). It is the Supplier's responsibility to contact the Destination Unit for verification.

(4) "ND Reduction line" and "ND Gas flow line flanges" to be defined after inspection in relation to the WRMP in which the "Heat Exchanger" is to be installed.

Continued on next page →

→ Continued from previous page

| - DESIGN DATA | - TYPE 1 | - TYPE 2 | - TYPE 3 | - TYPE 4 | - TYPE 5 | - TYPE 6 | - TYPE 7 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| - GAS FLOW - DESIGN FEATURES for WRMP with UPSTREAM OP of 24 bar |  |  |  |  |  |  |  |
| - Nominal pressure ANSI | - 300 | - 300 | - 300 | - 300 | - --- | - --- | - --- |
| - Max. line flow rate (Qlin) stm³/h | - 3,125 | - 7,190 | - 11,875 | - 14,375 | - --- | - --- | - --- |
| - Max operating pressure (MOPu) - bar | - 24 | - 24 | - 24 | - 24 | - --- | - --- | - --- |
| - Lower limit of minimum pressure (PuminL) bar | - 12 | - 12 | - 12 | - 12 | - --- | - --- | - --- |
| - Minimum pipe sizing pressure (PminP) bar | - 6 | - 6 | - 6 | - 6 | - --- | - --- | - --- |
| - Inlet/outlet pressure drop bar | - ≤ 5% PminP | - ≤ 5% PminP | - ≤ 5% PminP | - ≤ 5% PminP | - --- | - --- | - --- |
| - Max. gas flow speed m/sec | - ≤ 30 | - ≤ 30 | - ≤ 30 | - ≤ 30 | - --- | - --- | - --- |
| - Minimum/maximum permissible temperature (TS) °C | - -10 / +100 - (3) | - -10 / +100 - (3) | - -10 / +100 - (3) | - -10 / +100 - (3) | - --- | - --- | - --- |
| - Reduction line ND | - (4) | - (4) | - (4) | - (4) | - --- | - --- | - --- |
| - Gas flow line flanges ND | - (4) | - (4) | - (4) | - (4) | - --- | - --- | - --- |
| - Gas flow line flanges ANSI | - 600 RF | - 600 RF | - 600 RF | - 600 RF | - --- | - --- | - --- |

(3) The minimum design temperature of the "heat exchanger" must be verified prior to design (see standard UNI 9167: If the ambient temperature is less than -10 °C, the minimum design temperature may not be higher than the minimum ambient temperature). It is the Supplier's responsibility to contact the Destination Unit for verification.

(4) "ND Reduction line" and "ND Gas flow line flanges" to be defined after inspection in relation to the WRMP in which the "Heat Exchanger" is to be installed.

## Accessories

- Each heat exchanger must be equipped with:

- Water flow line:

  - Valve for draining the heating fluid;

  - Automatic air vent valve;

  - Inlet and outlet heating fluid temperature indicator. Scale 0÷120 °C;

- Gas flow line:

- Two vent valves with release to the atmosphere;

- Pressure indicator, on gas line, downstream of the heat exchanger (pressure gauge with scale 0÷100 bar; ½" gas connection; with ANSI 600 pressure gauge holder tap);

- Support system (Figure 2- base).

## Protective coating (painting)

- Each "heat exchanger" must be protected from external corrosion damage; in particular, it must be suitably painted with cycles and characteristics as listed below, with reference to Technical Specification T.S. 9982301_1 "ANTI-CORROSION PROTECTION OF METALLIC STRUCTURES ABOVE GROUND AND HORIZONTAL SIGNS ON THE FLOOR":

- High coefficient of adhesion to the surface to be protected;

- Good anti-corrosion properties;

- Reduced porosity and permeability to gases and liquids;

- Resistance to the persistent action of atmospheric and chemical agents;

- Base = RAL 7010 (grey) / Remaining = RAL 1016 (yellow).

- An example of a painting cycle is as follows:

- primer: zinc-based product;

- top coat: polyurethane-based paint.

## Machining tolerances

- The system of tolerances and couplings envisaged, except where design and processing requirements require specific tolerances, must comply with the following standards:

- UNI EN 22768 parts 1 and 2, or equivalents.

## Technical assessment

In relation to Legislative Decree 81/08, as amended and supplemented, Italgas Reti reserves the right, in its evaluation of the use of the proposed products, to consider the operational consequences deriving from the conditions of use of the equipment as prescribed by the Supplier in the "Use and Maintenance Manual".

# Marking

Each "Heat Exchanger" must bear the CE conformity marking in accordance with Legislative Decree no. 93 of 25 February 2000, as amended (Directive 2014/68/EU), Article 15.

In accordance with:

- Legislative Decree no. 93 of 25 February 2000, as amended / Annex I / point 3.3. / letter a)

An identification plate must be affixed to each "Heat Exchanger" on the shell, in an easily identifiable and readable position, indicating:

- Name and address or other distinguishing marks of the Manufacturer

- Type of "heat exchanger'"(Supplier's ref.);

- Year of manufacture;

- Maximum allowed pressure in bar;

- Rated output in kW;

- Capacity in litres on the shell side;

- Capacity in litres on the gas side;

- Empty weight in kg;

- Serial number or other identifying data of the heat exchanger.

It must also state:

- Purchase order number.

# Type Test

During the design phase of the product, it shall be the Supplier's responsibility to carry out at recognised laboratories or directly at the Supplier's premises all the "Type Tests" required by the reference standards and/or the Supplier's own design standards and the standards referred to therein, to verify the intended end use of the product.

# DOCUMENTATION REQUIRED FROM THE SUPPLIER

## Supplier()

- The potential Supplier must be qualified as an ITALGAS Supplier and must be able to provide after sales services directly in Italy.

## Documentation for the company approval process

The potential Supplier must submit the following documentation to the PROMA-CMMAT and/or PROMA-CMLASI Department:

- “Declaration of Conformity” with this technical specification and any specific documents (legislative provisions, applied standards, etc.) to which the supplier refers for the design and construction of the product, in accordance with the requirements of UNI CEI EN ISO/IEC 17050-1 (see the example in Appendix 1 to this technical specification).

In addition, the following documentation must be submitted to the SERTEC-NORM company Department:

- "EU Declaration of Conformity" in accordance with recent legislative decrees implementing the Directives applicable to the product (DBT, ATEX, RED, EMC, MID, RAEE, RoHS II, PED Directives etc.);

- Declaration of Conformity to Directive 2014/34/EU or Declaration of Exclusion from Directive 2014/34/EU (see example in APPENDIX 2 of this specification);

- Statement certifying ownership to market the product;

- Preliminary technical documentation describing the product, including information on the material, construction drawings, dimensional characteristics, tests and inspections required by the Supplier's standard, etc;

- Any list of references of the main customers using the proposed materials;

- Copy of the "EC type inspection certificate" for products for which the applied directives require the intervention of a Notified Body (e.g. ATEX);

- Whatever else the potential Supplier considers useful to better qualify the proposed product.

## Test Documentation

The Supplier must issue a “type 3.1” Inspection and Material Certificate in accordance with UNI EN 10204, which states that the products provided are compliant with the requirements of these specifications and which provides the test results.

Registration of the full production/test documentation completed by the Supplier must be kept (on the basis of legal provisions) for 10 years under its responsibility, and must be made available whenever requested by the Client.

## Supply Documentation

When supplying the "Heat Exchanger", the Supplier must provide the "DESTINATION UNIT” with the following: ()

- Documents compliant with Legislative Decree no. 286 of 21 November 2005, as amended.

- "EU Declaration of Conformity" in accordance with recent legislative decrees implementing the Directives applicable to the product (DBT, ATEX, RED, EMC, MID, RAEE, RoHS II, PED Directives etc.);

- Declaration of Conformity to Directive 2014/34/EU or Declaration of Exclusion from Directive 2014/34/EU (see example in APPENDIX 2 of this specification);

- “Type 3.1” Inspection and Material Certificates in accordance with UNI EN 10204;

- Copy of the "Installation, Use and Maintenance Manual" (in Italian) for the correct use of the product, conforming to the EC directives applied and/or Legislative Decree no. 81 as amended;

- Any other technical documents and/or drawings requested by the relevant Italgas Reti departments;

- Drawing showing the significant points for the ten-year shim checks (Gas side: Tube bundle, mouths, ellipsoidal cap);

- Inspection and quality plan and testing procedures.

# TESTS AND INSPECTIONS

The following tests and checks must be carried out on the components.

Italgas Reti reserves the right:

- To be present with its own Inspectors and/or Inspection Companies appointed by the same to carry out tests/checks c/o your plant and at your care and expense, to check the constructive and functional compliance of the materials in accordance with the specifications and/or reference standards.

- To verify, upon receipt and/or under actual conditions of use, the perfect compliance of the goods with the functional technical characteristics expressly indicated in the Contract.

The results and the manner in which the tests were carried out, as well as the precision class of the testing equipment (e.g. pressure recorder) used must be recorded in the “type 3.1” Inspection Certificate in accordance with UNI EN 10204.

## Dimensional inspection

The construction, dimensions and actual thicknesses must be checked against what is indicated in the exchanger drawings.

## Non-Destructive Testing (NDT)

All non-destructive testing operations indicated below must be carried out by qualified Level 2 personnel in accordance with formalised procedures. Level 2 personnel must be certified in compliance with UNI EN ISO 9712.

The non-destructive testing (NDT) to be carried out on welded joints subjected to pressure (of the shell and possibly the tube bundle) must include at least the following checks:

- All head-to-head welds, whether circumferential or longitudinal, on the exchanger body must be radiographed at 100% in compliance with UNI EN ISO 17636-1 (Class B); the acceptability level is level 1 according to UNI EN ISO 10675-1;

- All welds that cannot be radiographed must be checked 100% with liquid penetrants in accordance with UNI EN ISO 3452-1, acceptability level 1 to UNI EN ISO 23277 or with magnetic particles in accordance with UNI EN ISO 17638, acceptability level 1 according to UNI EN ISO 23278.

## Hydraulic testing

### Tube bundle hydraulic testing

The tube bundle must be hydraulically tested in accordance with point 7.4 of Annex I of Legislative Decree no. 93 of 25 February 2000, as amended.

The duration of the test must be at least 30 min.

### Shell hydraulic testing

The shell must be hydraulically tested in accordance with the provisions of point 7.4 of Annex I of Legislative Decree no. 93 of 25 February 2000, as amended.

The duration of the test must be at least 30 min.

## Paint inspections

Paint checks must be carried out as follows:

- Surface preparation in accordance with UNI EN ISO 8504;

- Roughness control in accordance with UNI EN ISO 8503;

- Thickness control according to ISO 19840 or equivalent standard.

## Right of the client

It is Italgas Reti's right, for each purchase order, to request from the Supplier:

- Further technical and/or graphic documentation,

- additional laboratory and/or field tests,

in order to verify the conformity of the proposed products with this technical specification and the cited standards to which reference is made.

# CONDITIONS OF SUPPLY

## Packaging

Supplier's Standard in compliance with Legislative Decree no. 152 of 3 April 2006 as amended and supplemented.

# REPLACEMENT SERVICE (On specific request)

## DESIGN AND EXECUTION OF REPLACEMENT WORKS

Following the award of the tender, the Builder/Contractor shall, after the necessary inspections and/or surveys, draw up the executive project to carry out the turnkey replacement and commissioning of the heat exchangers in full compliance with the topics defined in the following points.

The contract is inclusive of:

- the executive design of the works;

- the supply of heat exchangers to be installed;

- the dismantling and disposal of heat exchangers to be replaced;

- the transport and installation of the new "heat exchangers", any retrofitting of the existing system and commissioning of the same;

- the retrofitting/repair of any civil and mechanical works;

- the drafting (where necessary) of the Safety and Coordination Plan.

## MECHANICAL WORKS

The main activities concerning the operational execution for the replacement of deteriorated "heat exchangers" are as follows:

- On-site survey of the existing situation with special attention to the space available for the installation of the new "Heat Exchanger";

- Design and sizing of the "Heat Exchanger" and related plant materials required for functioning (e.g. counterflanges, pipe seals, etc.);

- Dismantling of the old "Heat Exchanger";

- Installation of the new "Heat Exchanger" with the gas-side exhaust conveyed to the outside by means of exposed piping;

- Commissioning.

## CIVIL WORKS (where necessary)

The executive project relating to the civil works of retrofitting/repair must be accompanied, at least, by the following documents:

- Technical report describing and illustrating the planned works, sizing of the structures;

- Architectural drawings of civil works complete with plans, elevations and cross-sections, etc.;

- Reinforced concrete calculations and the necessary documents for the C.A. (concrete building application) file at the Sportello Unico per l'Edilizia (SUE) (Building Permit Office), a service provided for under the Italian legal system governed by the Testo Unico dell'Edilizia (Consolidated Building Code) (Presidential Decree 380/2001);

- Construction details;

- Preparation of documentation for obtaining permits ();

- Time schedule of the works;

- Detailed estimated metric calculation of the works.

## DISPOSAL OF DECOMMISSIONED OR WASTE MATERIALS

The remaining decommissioned or leftover materials must be disposed of in accordance with the relevant legal provisions.

## GUIDELINES FOR DRAFTING/SUPPLEMENTING THE SAFETY PLAN

Depending on the executive design of each plant and the work phases foreseen for the realisation of the works, and based on the design drawings prepared by the Contractor, the Design Coordinator appointed by the Client shall integrate, update and sign the SCP (where necessary) (Legislative Decree no. 81/08 as amended), referred to in point 4.

# ReferenceStandards

      - Legislative Decree No. 85 of 19 May 2016 - "Implementation of Directive 2014/34/EU on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres".

      - Italian Legislative Decree no. 93 of 25 February 2000, as amended. “Implementation of Directive 97/23/EC on pressure equipment and Directive 2014/68/EU on the harmonisation of the laws of the Member States relating to the making available on the market of pressure equipment (recast), providing for its repeal” (so-called PED).

      - Legislative Decree No. 233 of 12 June 2003 - 'Implementation of Directive 1999/92/EC on minimum requirements for improving the safety and health protection of workers exposed to the risk of explosive atmospheres'.

- Legislative Decree No. 286 of 21 November 2005 as subsequently amended and supplemented. “Provisions for the regulatory reorganisation of the regulated liberalisation of the road haulage business”.

      - Italian Legislative Decree no. 152 of 3 April 2006, as amended “Environmental standards”.

      - Italian Legislative Decree no. 81 of 9 April 2008, as amended - “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”.

      - Ministerial Decree of 19 February 2007 - "Approval of the technical regulation on the chemical-physical characteristics and presence of other components in combustible gas to be transported".

      - Ministerial Decree of 16 April 2008 - “Technical regulations for the design, construction, testing, operation and supervision of works and distribution systems and direct lines for natural gas with a density not exceeding 0.8”.

      - UNI 9167 "Natural gas receiving, first reduction and measuring systems - Design, construction and testing".

      - UNI CEI EN ISO/IEC 17050-1 "Conformity assessment - Supplier's declaration of conformity - Part 1: General requirements”.

      - UNI EN 247 "Heat exchangers - Terminology".

      - UNI EN 305 "Heat exchangers - Definitions of heat exchanger performance and general test procedures for determining the performance of all types of heat exchangers"

      - UNI EN 306 "Heat exchangers - Methods for measuring the parameters needed to establish performance".

      - UNI EN 307 "Heat exchangers - Guidance for the preparation of installation, operation and maintenance instructions required to maintain performance of each type of heat exchanger".

      - UNI EN 12732 "Gas infrastructures - Welding of steel pipework - Functional requirements".

      - UNI EN ISO 22768-1 "General tolerances. Tolerances for linear and angular dimensions without individual tolerance indications".

      - UNI EN ISO 22768-2 "General tolerances. Geometrical tolerances for features without individual tolerance indications".

      - UNI EN 12186 "Gas transmission and distribution - Gas pressure regulating stations for transmission and distribution - Functional requirements".

      - UNI EN 12279 "Transport and distribution of gas - Gas pressure regulating installations on distribution networks - Functional requirements".

      - UNI EN ISO 3452-1 “Non-destructive testing - Penetrant testing - Part 1: General Principles”.

      - UNI EN ISO 23277 "Non-destructive testing of welds - Penetrant testing - Acceptance levels"

      - UNI EN ISO 17638 "Non-destructive testing of welds - Magnetic particle testing”.

      - UNI EN ISO 23278 "Non-destructive testing of welds - Magnetic particle testing - Acceptance levels".

      - UNI EN ISO 17636-1 "Non-destructive testing of welds - Radiographic testing - Part 1: X and gamma-ray techniques with film".

      - UNI EN ISO 10675-1 "Non-destructive testing of welds - Acceptance levels for radiographic inspection - Part 1: Steel, nickel, titanium and their alloys".

      - UNI EN ISO 9712 "Non-destructive testing - Qualification and certification of non-destructive testing personnel".

- UNI EN ISO 8504 - “Preparation of steel substrates before application of paints and related products - Surface preparation methods”.

- UNI EN ISO 8503 - “Preparation of steel substrates before application of paints and similar products - Surface roughness characteristics of blast cleaned steel substrates”.

      - UNI EN ISO 286-1 "Geometrical product specifications (GPS) - ISO code system for tolerances on linear sizes - Part 1: Basis of tolerances, deviations and fits".

      - UNI EN ISO 286-2 "Geometrical product specifications (GPS) - ISO code system for tolerances on linear sizes - Part 2: Tables of standard tolerance classes and limit deviations for holes and shafts".

      - ISO 19840 - "Paints and varnishes - Corrosion protection of steel structures by protective paint systems - Measurement of, and acceptance criteria for, the thickness of dry films on rough surfaces".

# APPENDICES

- APPENDIX 1 – “Sample Declaration of Supplier conformity with this Technical Specification”.

- APPENDIX 2 – “Sample Declaration of exclusion from Directive 2014/34/EU”.

# ATTACHMENTS

N.A.

## Appendix 1

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN ISO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(4)	S.T.V.F.C. 9991302	HEAT EXCHANGERS AND REPLACEMENT SERVICE

ON EXISTING PLANTS	Edition 2 of 15/06/2017

Additional information:

(5) 	...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(6) 	.............................................................			......................................................................................................................

(Name and position)				(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- List all the products for which approval for company use is requested (name, type, model), stating any codes assigned by the Supplier itself and, where existing, the relevant material codes assigned by Italgas Reti.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

## Appendix 2

ATEX Exclusion Declaration

We ..............................................................................................................................................................

(name of organisation)

with registered office in .............................................................................................................

(address)

as the .................................................................................................................................................

(Manufacturer / Authorised Representative)

declare under our sole responsibility that the products series

.....................................................................................................................................................................

.....................................................................................................................................................................

.....................................................................................................................................................................

(name, type or model, batch, group or serial numbers)

described in the Technical Specification / document(s)

.....................................................................................................................................................................

.....................................................................................................................................................................

(when necessary)

to which this declaration refers, comply with the following legislative / regulatory document(s)

.....................................................................................................................................................................

.....................................................................................................................................................................

(title(s) and/or number(s) and date(s) of publication of the standard(s) or other legislative and/or regulatory document(s))

and, according to Article 1, subsection 1a) of Directive 2014/34/EU of 26 February 2014 (Legislative Decree no. 85 of 19 May 2016) and Chapter 1 of ATEX 2014/34/EU GUIDELINES (first edition), based on an ATEX analysis (see subsection 32 of the aforementioned ATEX 2014/34/EU GUIDELINES), do not fall within the scope of the Directive 2014/34/EU, as they do not risk causing an explosion due to the lack of potential ignition sources, as defined in Standard UNI EN 1127-1, when used in systems that comply with the following legislative and/or regulatory documents

.....................................................................................................................................................................

.....................................................................................................................................................................

(title and/or number and date of publication of legislative and/or regulatory documents)

They can therefore be installed in all types of zones as defined in Legislative Decree no. 81 of 9 April 2008, as amended, Title XI (Directive 1999/92/EC of 16 December 1999).

.................................................................. 		..................................................................................................................................

(place and date of issue)		(name and signature or equivalent stamp of authorised person)

It is the Manufacturer's responsibility to define with its Notified Body the design, construction, testing and conformity assessment methods considered most appropriate.

DESTINATION UNIT means the TECHNICAL UNIT operating the reduction plant.

Supplier means the party responsible for the design and construction of the products or its legal representative as defined in Legislative Decree no. 206 of 6 September 2005 as amended and supplemented. - "CONSUMER CODE" pursuant to Article 7 of Law no. 229 of 29 July 2003.

DESTINATION UNIT means the TECHNICAL UNIT operating the reduction plant.

Submission to the Sportello Unico per l'Edilizia (SUE) (Building Permit Office) of the paperwork for obtaining authorisations is the responsibility of the Client.