“TECHNICAL SPECIFICATION”

S.T. 2327331

Variable pressure metering unit for gas network redelivery points supplied with upstream pressure between 0.15 and 5 bar

| Compiled by | SERTEC-NORM | GOZZANI, RICCARDO |
| --- | --- | --- |
| Checked by | SERTEC-NORM | VARESE, ENRICO |
| Checked by | MISURA-SVILMIS | GHIA, SERGIO |
| Checked by | PROMA/CMMAT | FASSINO, SILVIO |
| Checked by | PROMA-MATMA | SCOTTO, ENRICO |
| Checked by | SERTEC-LAB | SALATI, EUGENIO |
| Checked by | HSEQ | LIMONTA, AGOSTINO MASSIMO |
| Approved by | SERTEC | PISINO, FEDELE |

SUMMARY

1	PRELIMINARY INFORMATION	4

1.1	Cancels and replaces	4

1.2	Reason for issue	4

1.3	Company departments mentioned in the document	4

1.4	Definitions	4

2	PURPOSE AND FIELD OF APPLICATION	6

2.1	Purpose	6

2.2	Field of application	6

3	SPECIFICATIONS	7

4	TECHNICAL CHARACTERISTICS	7

4.1	Sizing criteria	7

4.1.1	General considerations	7

4.1.2	Design pressure	8

4.1.3	Diameters	8

4.2	Standard Units	9

4.3	Diagram of a variable pressure metering unit for Non-Interruptible Utility (VPMU)	12

4.4	Diagram of a variable pressure metering unit for Interruptible Utility (VPMUi)	14

4.5	Technical assessment	15

5	CONSTITUENT ELEMENTS	15

5.1	Circuit breakers	15

5.1.1	Electric circuit breakers	15

5.1.2	PE/steel transition joints	16

5.2	Shut-off devices	16

5.2.1	Upstream/Downstream measuring line and related by-pass	16

5.3	Filter	16

5.4	Blind disc	17

5.5	Gas meter (optional)	17

5.6	Straight sections of the measuring line	18

5.7	Electronic converter of gas volumes received	19

5.8	Remote reading module	20

5.9	Mains pressure safeguard system (optional)	20

5.9.1	Flow limiting device	20

5.9.2	Blocking valve	20

5.10	Pipes, joints and special parts	21

5.10.1	Materials	21

5.10.2	Joints	21

5.10.3	Control devices and accessories	22

5.11	Electrostatic discharge protection	22

6	MAXIMUM PERMISSIBLE ERRORS OF THE METERING SYSTEM	23

6.1	Maximum errors for gas meters	23

6.2	Maximum errors for "type 1" conversion devices	24

7	INSTALLATION OF EQUIPMENT	24

7.1	Filters	24

7.2	Measuring devices	24

7.3	Gas meters	24

7.4	Pneumatic connections	24

7.5	Protection against electrical disturbances	25

8	HOUSING	25

9	ABATEMENT OF ACOUSTIC EMISSIONS	26

10	Marking	26

11	TYPE TEST	27

12	APPROVAL PROCEDURE FOR COMPANY USE	28

12.1	Supplier	28

12.2	Documentation for the company approval process	28

12.3	Test Documentation	28

12.4	Supply Documents	28

13	TESTS AND INSPECTIONS	30

13.1	Visual and dimensional inspection	31

13.2	Mechanical strength test	31

13.3	Leak test	31

13.4	Non-Destructive Testing (NDT) of welded joints	31

13.5	Right of the Client	32

14	CONDITIONS OF SUPPLY	33

15	REFERENCE STANDARDS	34

16	Annex	37

17	APPENDICES	37

Appendix 1	38

Appendix 2	39

Appendix 3	40

# PRELIMINARY INFORMATION

## Cancels and replaces

This specification cancels and replaces Technical Specification 2327331, edition 2, dated 15.06.2017 “Variable pressure metering unit for gas network redelivery points supplied with upstream pressure between 0.15 and 5 bar”.

## Reason for issue

The update of the Technical Specification 2327331 and its reissue in the form of Technical Specifications, became necessary as a result of:

- adaptation of the housing to the new technical requirements of the Company.

## Company departments mentioned in the document

- PROMA-CMMAT = Materials

- SERTEC/NORM = Technical Services - Legislation

## Definitions

Cabinet:

A stainless steel/galvanised steel or plastic construction (see T.S. 9991310, point 4.1, letter a), soundproofed, for containment of the equipment constituting the Variable Pressure Metering Unit (VPMU), entirely above ground, inside which there is no personnel access.

Housing:

A normally soundproofed construction for containment of the equipment constituting the Variable Pressure Metering Unit (VPMU), with reduced dimensions, inside which there is no personnel access.

Metering unit:

Part of the system supplying the end user that is used for interception, gas metering and connection to the end user’s internal system. The metering unit consists of one or more units which, regardless of the technology used, are able to measure, convert the measured values, communicate and manage the gas supply.

VPMU:

Variable Pressure Metering Units (VPMU) that allow the supply of gas to industrial or similar users by connecting them directly to the Italgas distribution networks operated at a pressure between 0.15 bar (minimum pressure for the geometric sizing of the pipeline in M.P.A-Type 6) and 5 bar (maximum operating pressure of pipelines in M.P.B- Type 4).

Flow limiting device:

Equipment that limits the flow rate passing through the VPMU to prevent the pressure in the network supplying the unit from dropping below the contractually defined values.

Brick cabin:

Building with lightweight roof for the containment of all the mechanical works and metering systems entirely above ground.

Delivery flow rate (Qero):

Maximum flow rate to be measured by the VPMU at predetermined values of the minimum contractual pressure (Pcon).

Nominal flow rate of the plant (Qnom):

Flow rate that can be delivered by the metering unit at the nominal pressure for the geometric sizing.

Maximum allowed pressure (AP):

Maximum pressure for which the unit is designed (value specified by the manufacturer).

Maximum operating pressure (MOP):

Maximum pressure at which the plant can be used continuously and under normal operating conditions (5 bar relative).

Redelivery pressure (Pcon):

Minimum pressure at the redelivery point, for Metering Units serving the End Customer. This value is also used for the selection of the specific VPMU in relation to the maximum required flow rate of the unit (flow rate that can be delivered) and may not be lower than the minimum operating pressure of the road pipeline at or near the supply point of the unit.

Design pressure (DP):

Pressure value which design calculations are based on. This must be greater than or equal to the maximum allowed pressure.

Test pressure (Pcol):

Pressure at which the mechanical strength test of the "main gas circuit" is performed.

Re-delivery point:

Boundary point between the distribution plant and the end customer's plant where the distributor redelivers gas for supply to the end customer.

Blocking valve:

Equipment that blocks the flow passing through the VPMU to prevent the pressure in the network supplying the unit from dropping below the contractually defined values (to be installed on interruptible utilities only).

Measuring line:

Assembly of special parts, pipes and equipment suitable to contain the primary metering element, related accessories and control elements positioned before and after the straight sections upstream and downstream of the same.

It starts at the upstream shut-off valve and ends at the downstream shut-off valve, both valves included.

Conversion device:

A device constituting a sub-unit, installed on a gas meter that automatically converts the quantity measured at the measuring conditions into a quantity at basic conditions.

Operating pressure (OP):

Pressure present in the system under operating conditions.

For the other technical definitions contained in this specification, please see the standards listed in point 15 “Reference standards”.

# PURPOSE AND FIELD OF APPLICATION

## Purpose

The purpose of this Technical Specification is to define:

- the minimum design criteria considered by Italgas Reti for the sizing of VPMUs;

- the flow diagrams and system components in relation to the required capacity, the measurement pressure and the type of user (interruptible or non-interruptible);

- the range of use of standardised VPMUs in relation to specific supply conditions (pressure upstream of the VPMU);

- the acceptance criteria for company use.

- Compliance of the VPMUs with this Specification, with the applicable fire safety regulations and legal requirements for safety and environmental protection are essential basic requirements for the supply of VPMUs.

## Field of application

This Technical Specification applies whenever the opportunity arises:

- to purchase and approve for company use a new VPMU designed and manufactured by a new potential supplier in accordance with the requirements and indications contained in this specification;

- to provide the design criteria and constituent elements for the retrofitting of existing metering units. In such cases, the most suitable structure in relation to available space and overall conditions must be evaluated on a case-by-case basis.

# SPECIFICATIONS

- This specification must be understood as an integral part of the "ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS."

- This specification contains the minimum technical requirements demanded by Italgas Reti based on the reference Legislative and Technical Standards.

- It is the Supplier's responsibility to ensure that the products supplied fully comply with the provisions of this technical specification and the applicable standards.

- If the materials in question are supplied by an installer, the installer must document their compliance as required under “Documentation required from the Supplier”.

- It is the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. sharp edges or incorrect directions for use and maintenance, etc.), which may jeopardise the health and safety of the Client's workers (Legislative Decree no. 81/08, as amended and supplemented).

- for all technical and operational aspects that conflict with or are not mentioned in this technical specification but that nevertheless pertain to the design, installation, maintenance and use of the products themselves, it is the Supplier's responsibility to refer to the regulations in force.

# TECHNICAL CHARACTERISTICS

## Sizing criteria

### General considerations

The following sizing criteria take into account the operating conditions below:

- the gas and its additives, if any, are non-corrosive;

- the unit is subjected to stresses due to gas pressure and the effect of temperature variation;

- the design temperature is between –10°C and +60°C;

- environmental humidity up to 95%;

- unless otherwise specified, the flow rates refer to standard conditions with gas at 15°C and 1.01325 bar (absolute pressure).

The VPMU is designed to ensure correct gas measurement under operating conditions.

Continuity of supply is achieved by the installation of a general by-pass.

Each VPMU must:

- be constructed of materials suitable to withstand a maximum operating pressure (MOP) of 5 relative bar:

- guarantee the maximum required flow rate, in relation to contractually pre-determined minimum supply pressure values, depending on the type of pipe to which it is connected (see point 4.2: Tables 1, 2, 3 and 4) and in the system configuration complete with all the equipment provided for in the flow diagrams of points 4.3 and 4.4 (including the flow limiting device or blocking valve).

- consist of CE-marked pressure equipment (such as filters and shut-off valves provided on the VPMU) in accordance with the PED Directive (2014/68/EU), if the maximum operating pressure (MOP) exceeds 0.5 bar;

- comply, with regard to all the equipment, with the requirements of the ATEX Directives 2014/34/EU and 1999/92/EC where applicable.

Note:

Electrical equipment must be installed in accordance with CEI EN 60079-14 (CEI 31-33).

With regard to the sizing of the individual sections constituting the VPMU, please refer to the following points.

### Design pressure

Except in specific cases, the pressure value to be referred to for the geometric sizing of the unit and of the metering equipment is 0.15 bar.

### Diameters

#### Main measuring line

The VPMU must be sized so that, under operating conditions, the contractually defined flow and pressure values are guaranteed within the required accuracy class.

The gas speed must be kept within 25 m/s for the entire measuring line with a deviation of ±10% allowed.

#### Measuring line by-pass line (if any)

The by-pass line of the measuring line is sized according to the same criteria as the main line and must be the same length and have the same diameter as the main line.

The by-pass line of the measuring line must also provide a section for the possible installation of a meter with identical characteristics to the main meter; the installation of an additional filter for this is not required.

## Standard Units

Eight standard types of VPMUs are defined based on the criteria for sizing the individual components, the nominal flow rate range and interruptibility, as shown in Table1 below.

Nominal flow rate in Sm3/h (Qnom) of VPMUs

| Type VPMU | Material Code | Qnom |
| --- | --- | --- |
| VPMU 1 | 48002327818 | 110 |
| VPMU 1/i | 48002327819 |  |
| VPMU 2 | 48002327820 | 280 |
| VPMU 2/i | 48002327821 |  |
| VPMU 3 | 48002327822 | 445 |
| VPMU 3/i | 48002327823 |  |
| VPMU 4 | 48002327824 | 1120 |
| VPMU 4/i | 48002327825 |  |

Table1

DP = 0.15 bar

Note:

The 4 groups with an "i" in addition to the acronym VPMU with the related identification number, indicate the "interruptible" configuration.

The differences in construction between the two types of VPMU are highlighted in the diagrams in Figure 1 point 4.3 and Figure 2 point 4.4.

The use of each unit is envisaged for different flow rates depending on the minimum contractual supply pressure (Pcon) of the unit, in relation to the type of pipe it derives from (see Ministerial Decree 16/04/2008).

The tables below show these values broken down into units supplied by type 6 pipes (Table2) and those supplied by types 4 and 5 pipes (Table3):

Delivery flow rate in Sm3/h (Qero) from VPMUs depending on the contractual pressure (Pcon)

(MPA - type 6)

| VPMU type | Pcol 0.15 bar |  | Pcol 0.2 bar |  | Pcol 0.3 bar |  | Pcol 0.4 bar |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | max | min | max | min | Max | min | max | min |
| VPMU 1 | 110 | 6.2 | 115 | 6 | 125 | 5.8 | 134 | 5.6 |
| VPMU 2 | 280 | 16 | 292 | 15.7 | 315 | 15 | 340 | 14.5 |
| VPMU 2/a | 175 | 10 | 185 | 10 | 200 | 9 | 215 | 9 |
| VPMU 3 | 445 | 25 | 464 | 24 | 505 | 23 | 542 | 22.3 |
| VPMU 4 | 1120 | 62 | 1170 | 60.2 | 1265 | 58 | 1365 | 56 |
| VPMU 4/a | 725 | 39 | 760 | 38 | 820 | 37 | 880 | 36 |

Table2

Delivery flow rate Sm3/h (Qero) from VPMUs depending on the contractual pressure (Pcon)

(MPB - types 4 and 5)

| VPMU type | Pcol 0.5 bar |  | Pcol 1 bar |  | Pcol 1.5 bar |  | Pcol 2 bar |  | Pcol 3 bar |  | Pcol 4 bar |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | max | min | max | min | max | min | max | min | max | min | max | min |
| VPMU 1 | 145 | 5 | 195 | 4.7 | 240 | 4.2 | 290 | 3.8 | 390 | 3.3 | 485 | 3 |
| VPMU 2 | 365 | 14 | 485 | 12 | 605 | 11 | 730 | 10 | 975 | 9 | 1212 | 8 |
| VPMU 2/a | 230 | 9 | 310 | 7 | 390 | 7 | 465 | 6 | 620 | 5 | 770 | 5 |
| VPMU 3 | 585 | 22 | 780 | 19 | 975 | 17 | 1170 | 15 | 1560 | 13 | 1950 | 12 |
| VPMU 4 | 1460 | 54 | 1950 | 47 | 2435 | 42 | 2925 | 38 | 3900 | 33 | 4875 | 30 |
| VPMU 4/a | 950 | 34 | 1265 | 30 | 1585 | 27 | 1900 | 24 | 2530 | 21 | 3170 | 19 |

Table3

With reference to the flow charts in Figures 1 and 2, Table4 below shows the:

- nominal diameters of the upstream/downstream manifolds;

- general structure of the unit with reference to the constituent elements mentioned in points 4.3 and 4.5;

Geometric sizing of VPMUs

| Type VPMU | Qnom (Sm3/h) | Upstream section ND | Downstream section ND | Meter |  | Flow limiting device and/or blocking valve ND |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Class | ND |  |
| VPMU 1 | 110 | 50 | 50 | G 65 | 50 | 40 |
| VPMU 2 | 280 | 80 | 80 | G 160 | 80 | 50 |
| VPMU 2/a | 175 | 80 | 80 | G 100 | 80 | 50 |
| VPMU 3 | 445 | 100 | 100 | G 250 | 100 | 80 |
| VPMU 4 | 1120 | 150 | 150 | G 650 | 150 | 100 |
| VPMU 4/a | 725 | 150 | 150 | G 400 | 150 | 100 |

Table4

Note:

the dimensional characteristics in Table 4 are identical for both the "interruptible" and the "non-interruptible" type VPMUs.

The units VPMU 2/a and VPMU 4/a, compared to VPMU 2 and VPMU 4, provide for the installation of a turbine meter of a lower class according to Table 4 and the relevant flow rates are shown in Tables 2 and 3.

This does not apply to rotary piston meters.

## Diagram of a variable pressure metering unit for Non-Interruptible Utility (VPMU)

Figure 1: Diagram of a variable pressure metering unit for Non-Interruptible Utility (VPMU)

Note:

The choice of upstream section length (≥ 4  5 ND) is defined in point 5.6 of this specification.

Equipment list of VPMU in Figure 1

| Position | Description | Q.TY |
| --- | --- | --- |
| 1 | Dielectric joint or PE/steel upstream VPMU transition fitting | 1 |
| 2 | Upstream manifold | - |
| 3 | Shut-off valve upstream of filter and measuring line | 1 |
| 4 | Filter | 1 |
| 5 | Turbine or Rotary Piston Meter | 1 |
| 6 | Gas volume converter (PT conversion device) | 1 |
| 7 | Remote reading module | 1 |
| 8 | Thermometer pocket | 2 |
| 9 | Section predisposed for flow limiting device (see point 5.9) | 1 |
| 10 | Shut-off valve downstream of measuring line | 1 |
| 11 | Pressure gauge holder tap with cap | 2 |
| 11.1 | Pressure gauge holder tap with dial gauge | 2 |
| 12 | Downstream manifold | - |
| 13 | Dielectric joint or PE/steel downstream VPMU transition fitting | 1 |
| 14 | Shut-off valve upstream/downstream of measuring line by-pass | 2 |
| 14.1 | Spectacle blind disc | 1 |
| 15 | Measuring line by-pass with section predisposed for meter | 1 |

## Diagram of a variable pressure metering unit for Interruptible Utility (VPMUi)

Figure 2: Diagram of a variable pressure metering unit for Interruptible Utility (VPMUi)

Note:

The choice of upstream section length (≥ 4  5 ND) is defined in point 5.6 of this specification.

Equipment list of VPMUi in Figure 2

| Position | Description | Q.TY |
| --- | --- | --- |
| 1 | Dielectric joint or PE/steel upstream VPMU transition fitting | - |
| 2 | Upstream manifold | - |
| 3 | Shut-off valve upstream of filter and measuring line | 1 |
| 4 | Filter | 1 |
| 5 | Turbine or Rotary Piston Meter | 1 |
| 6 | Gas volume converter (PT conversion device) | 1 |
| 7 | Remote reading module | 1 |
| 8 | Thermometer pocket | 2 |
| 9 | Section predisposed for blocking valve (see point 5.9) | 1 |
| 10 | Shut-off valve downstream of measuring line | 1 |
| 11 | Pressure gauge holder tap with cap | 2 |
| 11.1 | Pressure gauge holder tap with dial gauge | 2 |
| 12 | Downstream manifold | - |
| 13 | Dielectric joint or PE/steel downstream VPMU transition fitting | 1 |

## Technical assessment

In relation to Legislative Decree 81/08, as amended and supplemented, Italgas Reti reserves the right, in its evaluation of the use of the proposed products, to consider the operational consequences deriving from the conditions of use of the equipment as prescribed by the Supplier in the "Use and Maintenance Manual".

# CONSTITUENT ELEMENTS

## Circuit breakers

In the case of connection to steel networks, electrical isolating devices are to be installed, PE/steel transition joints are to be provided for polyethylene networks.

### Electric circuit breakers

These are designed to electrically insulate the DVPMU from the underground steel pipe, cathodically protected.

Where provided, these consist of single-piece steel insulating joints with smooth ends to be butt-welded in accordance with UNI 10285 and Table M. 17850.. "Steel dielectric joint, NP 16, butt-weld ends".

Note: Electrical circuit breakers do not constitute part of the supply of the VPMUs covered by this T.S.

### PE/steel transition joints

Used when connecting to polyethylene networks, these are of the weld-on type on both materials and comply with the Technical Specification 1800300 “Polyethylene fittings and special parts for methane gas pipelines”. They must be of the weld-on type on both materials and comply in particular with standards:

- UNI EN 1555-2 for the polyethylene part;

- UNI EN ISO 3183 Grade PSL1 (L210 or qualitatively better) for the steel part.

Note: Transition joints do not constitute part of the supply of VPMUs covered by this Specification.

## Shut-off devices

### Upstream/Downstream measuring line and related by-pass

These consist of the shut-off valves upstream/downstream of the measuring line and upstream/downstream of the measuring line by-pass and have the following characteristics:

- butterfly type in accordance with UNI 11354 / UNI EN 593 or ball type in accordance with UNI 9734;

- Butt-weld smooth ends;

- minimum mechanical strength class: ANSI 150;

- direct control with removable lever;

- fast operation by 90° rotation of the obturator with end stops in fully open and fully closed position and indication of position reached;

- The use of grey cast iron as a material is not permitted.

## Filter

Compliant with UNI 10619-1, this consists of a device with the following characteristics:

- cylindrical body with horizontal axis;

- material: steel or aluminium alloy;

- minimum mechanical strength class of the filter body: NP 6;

- flanged connections NP16 / ANSI 150;

- maximum pressure drop, with clean filter element and at nominal system flow rate, ≤ 5% of contractual pressure.

The filtering capacity must be such as to ensure the correct functioning of the downstream equipment, and in any case such as to ensure that solid particles larger than 50 µm are stopped with filter cartridges complying with T.S. 9991300 "Cartridge filter elements for filters of gas reduction and metering units and plants".

The filter must be equipped with:

- differential pressure gauge clogging indicator, in accordance with T.S. 9991308 “Measuring and precision indicating instruments for plant installations”, fitted with graduated scale for direct reading of the pressure drop from upstream to downstream of the filtering element, electric reed contact as per SPDT, with storage of maximum Δp indicative of the clogging level reached and fitted with manifold;

- pressure intake on the filter outlet section, equipped with a pin pressure gauge holder tap and dial gauge, in accordance with T.S. 9991308 "Measuring and precision indicating instruments for plant installations", Bourdon spring type, metal case, watertight for assembly in the field, with threaded "gas" connection UNI EN 10226 ND 1/2", (NPT threaded not permissible), dial diameter 100 mm, with adequate full scale to allow easy and accurate reading of OPu, which must be between 25% ÷ 75% of full scale value, and maximum error not greater than 2.5% of full scale value;

- ball vent valve diameter ≥ 1/2" threaded "gas" UNI EN 10226 ND 1/2" (NPT threaded not permissible), with conveyable release fitted with steel blind cap, connected by means of a chain.

## Blind disc

A "figure-8" blind disc must be provided and installed immediately downstream of the upstream (gas direction) shut-off valve of the by-pass line of the measuring line. This consists of two steel disks, one blind and one through, joined in the form of spectacles, and with a handle, suitable for mounting between flanges, and with mechanical strength class ANSI 150 / NP 16.

## Gas meter (optional)

Standard installation involves the use of turbine speed meters, or alternatively rotary piston volumetric meters (these can be used up to and including class G650).

The meters must comply with T.S. 2401301 "Gas Turbine and Rotary Piston Meters" and the dimensional characteristics are shown in the table below:

Characteristics of the meters

| Meter size | Meter ND (mm) | Body flanging | Turbine meter length (mm) | Rotary Piston Meter Length (mm) |
| --- | --- | --- | --- | --- |
| G65 | 50 | ANSI 150 | 150 | 171 |
| G100 | 80 | ANSI 150 | 240 | 171 |
| G160 | 80 | ANSI 150 | 240 | 241 |
| G250 | 100 | ANSI 150 | 300 | 241 |
| G400 | 150 | ANSI 150 | 450 | 450 |
| G650 | 150 | ANSI 150 | 450 | 450 |

Table5

Different types of meters may be used subject to prior authorisation by the SERTEC-NORM Department, provided that they comply with the legal requirements, performance and functional characteristics defined by the laws and standards in force (see T.S. "“Turbine and Rotary Piston Meters”).

## Straight sections of the measuring line

The ND of the pipe of the straight sections upstream and downstream of the meter must be equal to the ND of the meter required to regularly measure the delivery flow rate; the minimum lengths to be complied with, excluding valves, are:

upstream section:

- for turbine meters: 5 ND (2 ND if confirmed by the Supplier);

- for rotary piston meters: 4 ND.

Sufficient space must be provided before the 45 ND for the insertion of the pressure control intake.

downstream section:

- for all meter types: 2 ND.

Sufficient room must be provided after the 2 ND for the insertion of the two thermometer pockets, for measuring and control purposes.

## Electronic converter of gas volumes received

This must comply with the T.S. TC-1/681 "Electronic gas volume converters".

It is a microprocessor-based electronic device that corrects the volume of the gas received back to standard cubic metres, calculated at 15 °C and 1.01325 bar.

This device, associated with a gas meter from which it obtains volume repetition via a low-frequency pulse emitter, is classified depending on its components into:

- "Type 1" integrated electronic gas volume conversion device, in which the pressure and temperature sensors are located inside the apparatus, i.e. are an integral part of it.

- "Type 2" modular electronic gas volume conversion device, in which the pressure and temperature sensors are external to the apparatus, i.e. they are separate (and interchangeable) components.

Electronic gas volume converters must be MID approved (2014/32/EU), comply with the provisions of AEEGSI Resolution - ARG/gas 155/08 as amended, UNI EN 12405-1, UNI/TS 11291 and related technical standards.

The electronic gas volume converter provided for VPMUs is Type 1 according to UNI EN 12405-1 with internal/external pressure transducer and external temperature probe.

The models allow gas volumes to be converted, using the quantities of Pressure (P), Temperature (T) and Gas Compressibility (Z), according to the values measured in the field or set in the device.

They are then further classified into:

- T		Acquired variable: temperature, P and Z set fixed;

- PT	Acquired variables: pressure and temperature, Z is set fixed;

- PTZ	Acquired variables: pressure, temperature and Z (set and recalculated as a function of P and T).

The electronic gas volume conversion devices may also have an incorporated data-logger section, in which the data for Corrected Volume, Non-corrected Volume, Pressure, Temperature and Flow Rate are recorded every 15 minutes on an hourly basis, and stored for a period in accordance with the requirements of UNI/TS 11291-4. The performance that a gas metering system must have on an hourly basis is indicated in UNI/TS 11291-4 which refers, as far as gas volume converters are concerned, to UNI EN 12405-1 and applies to metering units with a flow rate greater than 65 m3/h (G40 meter).

They can also be prepared for subsequent connection or already be equipped with a data transmission section (modem), either via RS 232 serial output with a communication vector consisting of a telephone line (twisted pair) or via GPRS/GSM with a communication vector consisting of a mobile telephony network, in compliance with the regulations in force.

The conversion device is recognised as a sub-assembly that functions independently and constitutes a measuring instrument together with other sub-assemblies with which it is compatible in accordance with Legislative Decree no. 22 of 2 February 2007, as amended, and is subject to periodic verification as established by Ministerial Decree no. 93 of 21 April 2017, as amended.

## Remote reading module

In addition to the Data-Logger section, a remote reading module must also be provided for transmitting data and sending them to the Supervision Centre for information acquisition.

The metering system must be equipped, for the remote transmission of recorded data, with technologies and methods that offer sufficient guarantees in terms of their protection from access by third parties and of correspondence between data transmitted and received by means of transmission via fixed or mobile telephony, SMS, etc.; data transmission must be instantaneous or on demand.

This transmission system must be agreed upon and compatible with the existing data acquisition systems and processing software in use at Italgas Reti.

## Mains pressure safeguard system (optional)

The installation of such a system is evaluated by Italgas Reti on a case-by-case basis according to the actual needs of the gas network.

The VPMU must therefore be supplied with construction solutions considering the above choice, namely:

- with a section predisposed for future installation of the system in points b) or c);

- with the installation of a flow limiting device in the case of a "non-interruptible" utility;

- with the installation of a minimum pressure block in the case of an "interruptible" utility;

### Flow limiting device

The equipment limits the flow rate through the VPMU depending on the pressure at the system inlet.

The use of pressure regulators approved for company use is allowed, in accordance with the T.S. 23273 "List of pressure reducers-regulators approved for company use”, suitably modified to perform the required function and with the following characteristics:

- diaphragm type with spring-loaded contrast and/or pilot operation;

- steel or spheroidal cast iron body;

- minimum mechanical strength class: NP 16 / ANSI 150;

- flanged connections;

- manual adjustment, from the outside, of the set pressure (in the range defined depending on the network supplying the system: MPA or MPB).

- Under normal operating conditions, the obturator is in the fully open position; choking begins, until complete closure, when the inlet pressure value is below the set-point.

The pilot, if present, must be supplied by a stabiliser unit with a filter having suitable characteristics for correct operation and must have the following characteristics:

- upstream pressure range: 0.15 ÷ 5 bar (defined based on the network supplying the system: MPA or MPB)

- pressure stabiliser to maintain a constant pilot supply pressure (can be built into the pilots);

### Blocking valve

It consists of a device with the following features:

- steel or spheroidal cast iron body;

- minimum mechanical strength class: NP 16 / ANSI 150;

- flanged connections;

- manually adjustable automatic switching device (e.g. diaphragm pressure switch with contrast spring and impulse tap connection).

## Pipes, joints and special parts

The pipes, with related fittings, special parts and component materials, must comply with the requirements set out in the Ministerial Decree of 16 April 2008 and comply with the following specifications:

- S.T.V. 15AA300 “Welded steel pipes for natural gas pipelines”;

- S.T.V.F.C. 17AA300 “Steel fittings”.

They must also be suitable for the intended use in accordance with the regulations in force.

### Materials

The materials must be suitable for the intended use. Pipes with the related fittings and special parts must be made of steel, unless otherwise specified, and subjected to a suitable surface paint treatment. The use of spheroidal cast iron is allowed.

Instrument connection tubes and impulse taps may be made of material other than steel, provided they are metallic (e.g. copper); they must be joined by welding or by suitable mechanical couplings.

### Joints

All connecting joints of the pipes with each other and/or with the equipment constituting the VPMU must be designed and manufactured in such a way as to guarantee a perfect seal over time, even in the presence of vibrations and/or mechanical stresses to which the system elements may be subjected.

The number of threaded joints (which may never be used for pipes with ND ≥ 50) must be kept to a minimum in order to reduce the possibility of gas leaks from the system. These joints must comply with UNI EN 10226. To ensure a better seal, hemp with suitable, long-lasting glues, polytetrafluoroethylene tape or other equivalent materials specifically declared suitable according to UNI EN 751-3 may be applied to the ends.

In order to limit micro-dispersion phenomena not detectable by instrumental tests, joints made with compression fittings must have equivalent sealing and reliability characteristics to those of ferrule fittings.

Unless otherwise specified, the instrument connection tubes must be joined by welding or suitable mechanical couplings.

Welded connections must comply with standards and qualified procedures.

Flange joints must comply with applicable laws, directives and standards, taking into account the technical/construction characteristics of the individual piece of equipment.

These characteristics, which must be adhered to when selecting flanges, are indicated, where present, in the various chapters of this Technical Specification.

### Control devices and accessories

- Pressure control gauge intakes

These are located on the manifold upstream of the shut-off valve upstream of the filter, on the manifold downstream of the shut-off valve of the measuring line and at other suitable points for pressure control of the VPMU and consist of:

- section of quality steel pipe, normally not smaller than ND ½", with one end edge-welded to the pipe, in a front or side position and not at the rear, and the other end "gas" threaded in accordance with UNI EN 10226 (NPT threaded not allowed);

- ½˝ pin stopcock, also "gas" threaded UNI EN 10226 (NPT threaded not allowed), at both ends;

- end cap with ½˝ chain.

- Pressure intakes with pressure gauge

These are located downstream of the filter and downstream of the flow meter after the thermometer pockets; they consist of the same elements as described in point a) and of:

- a dial pressure gauge, in accordance with T.S. 9991308 "Measuring and precision indicating instruments for plant installations", Bourdon spring type, metal case, watertight for assembly in the field, with threaded "gas" connection UNI EN 10226 ND 1/2", (NPT threaded not permissible), dial diameter 100 mm, with adequate full scale to allow easy and accurate reading of OPu, which must be between 25% ÷ 75% of the full scale value, and maximum error not greater than 2.5% of the full scale value.

- Temperature intakes

These are located downstream of the measurement, at a distance of more than 2 ND from the gas meter, are provided for the fiscal measurement and control of the gas flowing in the VPMU, and consist of:

- section of gas threaded quality steel pipe UNI EN 10226 (NPT threaded not allowed) welded to the gas supply pipe;

- stainless steel thermometer pocket machined from a bar, into which the temperature sensor referred to in point 5.10 of this T.S. can be inserted and removed for temperature measurement without interrupting the gas flow, with threaded gas terminal ½" UNI EN 10226 (NPT threaded not allowed).

The thermometer pockets must be filled with fluid mineral oil, have appropriate mechanical properties and dimensions, and insertion depth at least 1/3 of the nominal pipe diameter.

Thermometer pockets without the sensor element must be fitted with a quality steel plug.

The pockets must be installed on the upper generatrix of the pipe in a vertical position. For pipes with ND≤100 only, installation at a 90° bend or at an angle of 45° to the pipe axis is allowed.

The sensor elements considered, totally immersed in the gas flow, are:

- the bulb containing the sensor liquid (not mercury) for the control thermometer;

- the "PT 100'"thermoresistance (or others) with or without transmitter.

## Electrostatic discharge protection

In order to ensure protection against the build-up of electrostatic discharges, the VPMU must be equipped with an earth connection.

In the case of installation in a metal cabinet, the connection can be made between the cabinet and an anchor bolt to the base.

This connection must be made with a yellow-green copper cable with a minimum cross-section of 4 mm2, PVC or G7 rubber insulated of an adequate length, fitted with cable lugs at the brass ends.

# MAXIMUM PERMISSIBLE ERRORS OF THE METERING SYSTEM

The maximum permissible errors of the metering system are those stipulated in the respective product standards and in accordance with current metric legislation.

Gas meters and gas volume conversion devices must comply with the requirements of the applicable MID Directive and bear the CE marking and supplementary metrology marking (the capital letter "M" followed by the last two digits of the year of affixing of the marking, inscribed in a rectangle).

## Maximum errors for gas meters

The maximum permissible errors for gas meters are those defined in the Technical Specification 2401301 "Turbine and Rotary Piston Gas Meters", in accordance with product standards and current legislation.

Gas meters are subject to periodic inspections in accordance with Decree no. 93 of 21 April 2017, as amended, and standard UNI 11600.

## Maximum errors for "type 1" conversion devices

The maximum permissible errors for "type 1" conversion devices must be in accordance with UNI 12405-1:

Maximum permissible errors (%) for "type 1" conversion devices

| Type of device | Maximum error under reference conditions | Maximum error under operating conditions |
| --- | --- | --- |
| PT or PTZ device | 0.5 | 1 |

Table 6: Maximum permissible errors (%) for "type 1" conversion devices

"Type 1" conversion devices are subject to periodic inspections in accordance with Decree no. 93 of 21 April 2017, as amended, and standard UNI 11600.

Note:

- The error of the gas meter was not taken into account;

- All % values refer to the measured value.

# INSTALLATION OF EQUIPMENT

The installation of the equipment and any pneumatic connections must be carried out following the instructions provided by the Manufacturers and the criteria below. Access for future tests and calibration must also be guaranteed.

## Filters

Equipment releases must extend outside the cabinet or cabin, if any, in a position to ensure maximum safety and easy collection of any impurities.

## Measuring devices

Measuring instruments and primary elements must be installed in an easily accessible position so as to easily allow data collection and control and calibration operations.

Measuring instruments (converters, etc.) must be suitably protected within suitable housings which must comply with the requirements of point 8 and have dimensions and expedients such as to prevent temperature variations outside the limits defined by the manufacturer.

## Gas meters

The gas meter must be installed so as to avoid any mechanical stress caused by upstream and downstream piping and in accordance with the manufacturer's instructions.

The measurement pressure must be taken via the "Pr" tap on the meter.

In the case of rotary piston meters, the operating pressure must be measured upstream of the upstream straight section of the meter if not equipped with a dedicated Pr intake.

## Pneumatic connections

The pneumatic connections of the measuring instruments must have a minimum slope of 8% towards the connection point on the main line or towards the condensate separator/collector tanks.

## Protection against electrical disturbances

To ensure reliable operation, the metering system must be complete with the necessary protection against electrical disturbances, both on the inlet and outlet circuits.

For example, the following may be used for this purpose:

- voltage suppressors that also offer protection against overvoltages, station switching and short circuits on MV or HV lines;

- network filters that must be able to attenuate both symmetrical and asymmetrical interference;

- TVSS (Transient Voltage Surge Suppressor), consisting of filters and varistors, for absorbing high amounts of energy and with a high operating speed in the event of rapid impulse growth (compliant with standard CEI EN 61643-11 (IEC 37-8)).

The risk assessment to establish the need for lightning protection systems (LPS) and the criteria to be adopted for their possible implementation are contained in IEC Standards 81-10/1, 81-10/2, 81-10/3 and 81-10/4.

# HOUSING

The VPMU can be installed either in a single cabinet or in several separate cabinets for each plant section (mechanical works, fiscal measurement, etc.).

The housing/cabinet must be constructed of materials with a reaction to fire rating not greater than 1, in accordance with Ministerial Decree of 26 June 1984 as amended and T.S. 9991310 (e.g. galvanised sheet metal, fibreglass, brick, etc.), provided it is designed in such a way as to give the structure good stability characteristics against adverse weather conditions (snow, wind, etc.), and subject to the more stringent requirements contained in this T.S.

Ventilation must be achieved by means of openings in the doors, distributed at the top and bottom. In the event that the soundproofing panels in front of the upper openings interfere with equipment constituting the VPMU, such openings may be made in an strip above the doors. The openings must have a total surface area of at least 20% of the floor surface, and at least such that the classification of explosion hazard locations (in accordance with CEI EN 60079-10-1) is the least onerous possible (preferably zone 2 inside the housing and a non-hazardous location outside, for the installation of a cabinet for electrical and electronic equipment envisaged in this T.S. adjacent to at least one of the two smaller sides).

Ventilation grilles may be constructed without rain deflectors in compliance with the presence of free openings, protected with spark guard netting.

The cabinet must be adequately lined internally (including the cover panel) with soundproofing fireproof panels, which, in the case of "mineral fibre/glass'"cladding, must be ≥ 25 mm thick. This cladding must in any case be protected by a containment wire mesh/grid. In order to maintain the functionality of the ventilation openings, special panels (one for each opening) must be provided, suitably spaced (≥ 15 mm) from the soundproofing panel of the door, and no larger than 180 mm on each side in relation to the openings. The cabinet is an integral part of the VPMU supply. There is no personnel access to the inside of the cabinet, but the two larger sides must be fully openable to the outside with two- or three-leaf doors. Door leaves must have a minimum net opening height of 1700 mm, and must be equipped with a blocking system in the open position at an angle ≥ 90°. One end of the blocking system must be fixed to the cabinet frame (e.g. with a chain or hinged). Above and/or below the doors, one or two 100 mm high strips may be made, if necessary for the construction-static purposes of the housing, for improved connection with the vertical walls of the cabinet, without prejudice to the minimum opening height of the doors.

The doors of the housing/cabinet must be fitted with a VIRO 8211 latch lock with F33642 key, in order to allow manoeuvring, checks and normal maintenance operations.

# ABATEMENT OF ACOUSTIC EMISSIONS

In relation to the need to comply with the legal provisions in force, regarding noise pollution of the environment (sound emissions), the VPMUs must comply, by means of the expedients deemed most suitable by the Supplier (e.g. soundproof cabinets, etc.) with the following maximum permitted sound emission levels under conditions of maximum output:

| Noise emission level from standard VPMUs |  |
| --- | --- |
| Distance from cabinet walls: 2 m | Distance from cabinet walls: 10 m |
| dB(A) = 70 | dB(A) = 60 |

Although the above is not the standard solution, Italgas Reti may specifically request, with a separate quotation to be indicated in the offer phase, the supply of plants meeting more stringent noise emission levels indicated below, depending on the requirements imposed by current legislation.

| Noise emission level from standard VPMUs |  |
| --- | --- |
| Distance from cabinet walls: 2 m | Distance from cabinet walls: 10 m |
| dB(A) =60 | dB(A)  50 |
| dB(A) =50 | dB(A)  40 |

# Marking

An identification plate must be affixed to each "Variable Pressure Metering Unit" in a position which is easy to identify and read, indicating:

- Type of "Variable Pressure Metering Unit" (Supplier's ref.);

- Maximum operating pressure (MOP);

- Design pressure;

- Operating pressure (OP);

- Nominal Flow Rate of the Plant, expressed in Sm3/h;

- Year of construction;

- Weight in kilograms;

- Serial number or other identification data of the Variable Pressure Metering Unit;

- Purchase order number and position.

Similarly, on each main piece of equipment composing the VPMU, such as valves, filters, blocking devices etc., an identification plate must be affixed containing, as a minimum requirement, the following data:

- Manufacturer's name and/or trademark;

- Type and model of equipment;

- Year of construction;

- Features (see Supplier's);

- Serial number or other identifying data;

- Pressures (max. supply, operating, flanging, etc.);

- Nominal flow rate expressed in Sm3/h;

- Calibration range;

- Operating temperature range;

- Any references for spare parts (e.g. filter cartridge, etc.).

The constituent elements of a VPMU subject to this Technical Specification must be provided with the markings required by the EU Directives, where applicable, and by the relevant applicable technical standards, considering that the affixing of the CE marking, together with any other markings that may be used, is subject to the provisions of Decision no. 768/2008/EC of 9 July 2008 on a common framework for the marketing of products and implemented by the legislative decrees transposing the applicable product directives, a non-exhaustive list of which is given under "Legal references" in this Technical Specification.

They must therefore bear the conformity marking , affixed in the manner provided for by the legal provisions in force, together with any other markings provided for by the same directives.

# TYPE TEST

During the design phase of the VPMU, it will be the Supplier's responsibility to carry out at recognised laboratories or directly at the Supplier's premises all the "Type Tests" envisaged by the reference standards and/or the Supplier's own design standards and the standards referred to therein to verify the intended end use of the VPMU.

Note:

“Type tests” are not envisaged in the event that Italgas Reti deems that any modifications made by the Supplier to the VPMUs already accepted for company use, affecting the structure and/or the arrangement of the piping connecting the equipment, do not affect the functionality, safety and reliability of the VPMU.

# APPROVAL PROCEDURE FOR COMPANY USE

## Supplier

- The potential Supplier must be qualified as an ITALGAS RETI Supplier and must be able to provide after sales services directly in Italy.

## Documentation for the company approval process

The potential Supplier must submit the following documentation to the PROMA-CMMAT Department at the tender stage:

- “Declaration of conformity” with this technical specification and any specific documents mentioned in it (legal provisions, applied standards, MID Directive, ATEX, EMC, PED, etc.) to which the supplier refers for the design and construction of the product, as indicated in the UNI CEI EN ISO/IEC 17050-1 standard (see the example given in Appendix 1 of this technical specification);

## Test Documentation

The Supplier must issue a “type 3.1” Inspection and Material Certificate in accordance with UNI EN 10204, stating that the VPMU supplied are compliant with the requirements of these specifications as well as the legislative provisions as per point 15.

The Supplier must also produce a test report containing at least the following information:

- Name of the authorised person responsible for the test;

- Test date;

- System manufacturer;

- Identification of the section to which the test relates;

- Design pressure;

- Pressure reached during the test and the period of time for which it was maintained;

- Test fluid;

- Test results;

- Reference to the test procedure (if any);

- Instrumentation used for the test with indication of calibration validity;

- Type and serial number of the instrument used for the test.

Registration of the full production/test documentation completed by the Supplier must be kept (on the basis of legal provisions) for 10 years under its responsibility, and must be made available whenever requested by the Client.

## Supply Documents

- Documents compliant with Legislative Decree no. 286 of 21 November 2005, as amended;

- "EU Declaration of Conformity" in accordance with recent legislative decrees implementing the Directives applicable to the product (e.g. MID, ATEX, EMC, PED Directives etc.).

  - If, on the basis of the design of a project intended for use under pressure (Directive 2014/68/EU), the Supplier determines that its product does not have the characteristics defined by the aforementioned directive, it must in any case submit a declaration of inclusion within art. 3 paragraph 3 of the aforementioned directive to certify the exemption of the product in compliance with the provisions of the same paragraph (see the example in Appendix 3 of this Technical Specification).

  - If, on the basis of the design of a product intended for use in potentially explosive atmospheres (Directive 2014/34/EU), the Supplier determines that its product does not fall within the requirements of the aforementioned directive, the Supplier must submit a declaration of assumption of responsibility (see the example in Appendix 2 of this Technical Specification) which certifies that, following the risk analysis carried out, the product does not have any potential ignition sources of its own, and therefore does not fall within the scope of Legislative Decree no. 85/2016 (Directive 2014/34/EU) and can therefore be installed in all the zone types referred to in Legislative Decree 233/03 (Directive 1999/92/EC).

- Possible certificate issued by Notified Body with relevant CE marking identification number;

- Any list of references of the main customers using the proposed materials;

- Statement certifying ownership to market the product;

In addition, for each individual VPMU, upon delivery the Supplier must provide to the DESTINATION UNIT a technical file (Data Book) containing at least the following documentation:

- Certificate of calibration and alignment in the required measuring range;

- “Type 3.1” Inspection and Material Certificates in accordance with UNI EN 10204;

- User and maintenance manual in Italian of the various equipment which, for pressure equipment, complies with points 3.3 and 3.4 of Annex I to Legislative Decree no. 93 of 25 February 2000, as amended;

- Functional diagram, construction drawing (total overall dimensions of the unit including centre distance between inlet and outlet pipes) and equipment list with materials used;

- Declaration of conformity with applicable legislation;

- Declaration of conformity of installed equipment with applicable directives;

- Declaration of conformity with UNI 10619;

- Leak test report;

- Recommended spare parts list of equipment subject to preventive maintenance;

- For equipment covered by the PED Directive 2014/68/EU (e.g. filters), for which at least two of the following conditions arise:

    - Internal diameter in mm or nominal dimensions 500 or less;

    - Maximum allowed pressure AP 6 bar or less;

    - The product of the internal diameter in mm or nominal dimensions ND times the maximum allowed pressure 3000 or less,

the Supplier must make available the documentation containing the basic data and construction characteristics (e.g. thicknesses) required to carry out integrity checks of the various components (external equipment body, ellipsoidal caps, etc.) of the pressure equipment.

- Whatever else the potential Supplier considers useful to better qualify the VPMU.

# TESTS AND INSPECTIONS

Italgas Reti reserves the right:

  - To be present with its own Inspectors and/or Inspection Companies appointed by the same to carry out tests/checks c/o your plant and at your care and expense, to check the constructive and functional compliance of the materials in accordance with the specifications and/or reference standards.

  - To verify, upon receipt and/or under actual conditions of use, the perfect compliance of the goods with the functional technical characteristics expressly indicated in the Contract.

It is understood that the favourable outcome of our inspection and checking of the materials shall not release you in any way from the responsibilities and obligations arising from each individual contract.

The tests and inspections described below must be carried out by the Supplier on each VPMU supplied:

- Visual and dimensional inspection (point 13.1);

- Mechanical strength test (point 13.2);

- Leak test (point 13.3);

- Functional testing of individual pieces of equipment and/or the fully assembled system with regard to maximum flow rates (compatibly with laboratory equipment) and pressure drops. The tests must be certified in accordance with UNI EN 10204 “type 3.1”;

- Repeated tests to verify the accuracy and reliability of intervention of the flow limiting device and/or pressure block;

- Non-destructive testing of welds (point 13.4).

## Visual and dimensional inspection

The construction and dimensional conformity with the construction drawing must be checked.

The dimensional tolerances of the threads must be those specified in the relevant standards.

The inspections must be certified in accordance with UNI EN 10204 “type 3.1”.

## Mechanical strength test

Before the installation is assembled, the main circuit of each VPMU must undergo a mechanical strength test at the factory, which must be recorded. Test procedures must be chosen according to UNI EN 12327.

The mechanical strength test must have a minimum duration of 4 hours, after temperature stabilisation, and must be performed under the conditions specified below:

- 7.5 bar, for the entire VPMU circuit.

The test can be performed by means of a hydraulic test or by using air or inert gases.

The mechanical strength test is not required for:

- filters, meters, flow limiting device and/or pressure block,

for which factory testing must be carried out in accordance with the relevant standards.

If the Supplier can prove by means of suitable existing documentation that the components of the main circuit have been previously tested at least to the required test pressure, the strength test need not be repeated on these components.

## Leak test

After the strength test, all the components that were removed from the installation before the test must be reinstalled.

The entire installation must be subjected to a leak test at a pressure at least equal to the operating pressure. The pressure limit for the leak test must be that which occurs under normal operating conditions in each section of the installation.

The test must have a minimum duration of 30 minutes, after temperature stabilisation.

Air or inert gas or mains gas must be used as the test fluid.

## Non-Destructive Testing (NDT) of welded joints

Welding of steel pipes must be carried out in accordance with UNI EN 12732, according to qualified procedures complying with UNI EN ISO 15614-1 or equivalent standards.

Welders must be qualified in compliance with UNI EN ISO 9606-1 or equivalent standards.

The Supplier must carry out non-destructive testing of the welds of the  plants at its own expense, in accordance with the relevant standards.

All non-destructive testing operations must be carried out by qualified Level 2 personnel in accordance with formalised procedures. Level 2 personnel must be certified in compliance with UNI EN ISO 9712.

The non-destructive testing (NDT) to be carried out on welded joints subjected to pressure must include at least the following checks:

- Head-to-head welds must be radiographed at 20% in accordance with Italgas Reti and in compliance with UNI EN 17636-1 (Class B); the acceptability level is level 1 according to UNI EN 10675-1.

- Any welds that cannot be radiographed must be checked 100% with liquid penetrants in accordance with UNI EN ISO 3452-1, acceptability level 1 to UNI EN ISO 23277 or with magnetic particles in accordance with UNI EN ISO 17638, acceptability level 1 according to UNI EN ISO 23278.

As regards the quality of the welded joints, Italgas Reti reserves the right, at the moment of accepting the VPMUs, to have an inspection of the welded joints carried out in the presence of its own inspectors, with non-destructive testing (e.g. radiographic tests).

The results of any tests already carried out by the Supplier are accepted provided that the joints indicated by Italgas Reti coincide with those subjected to the tests.

## Right of the Client

It is Italgas Reti's right, for each purchase order, to request from the Supplier:

- Further technical and/or graphic documentation,

- additional laboratory and/or field tests,

in order to verify the conformity of the proposed products with this technical specification and the cited standards to which reference is made.

# CONDITIONS OF SUPPLY

Within the supply limits, VPMUs must be suitably pre-assembled; if they are not to be housed in a cabin or brick prefab, they must be supplied on a suitably designed and manufactured metal skid in order to:

- discharge the entire weight of the VPMU onto the concrete base provided to secure the housing cabinet;

- allow and facilitate the operation of shut-off devices as well as the inspection and maintenance of filtering and measuring equipment.

The arrangement of the equipment must be such as to allow for the proper functioning of the measuring unit. The maximum height of the pre-assembled measuring system should not exceed h max = 1.9 m from the floor.

The equipment must be assembled according to good engineering practice.

In particular, the layout of the pipes must not give rise to additional stresses on the equipment connected to them.

# REFERENCE STANDARDS

- Law 26/10/95 no. 447 “ Framework Law on Noise Pollution".

- Legislative Decree no. 22 of 02 February 2007, as amended. – "Implementation of Directive 2004/22/EC on measuring equipment and Directive 2014/32/EU of 26 February 2014 as amended by the delegate directive (EU) 2015/13 of 31 October 2014 on the harmonisation of the laws of the Member States relating to the making available on the market of measuring equipment (recast), providing for its repeal".

- Legislative Decree no. 152 of 3 April 2006, as amended and supplemented – "Environmental standards".

- Legislative Decree no. 286 of 21 November 2005, as amended. “Provisions for the regulatory reorganisation of the regulated liberalisation of the road haulage business”.

- Legislative Decree no. 85 of 19 May 2016 – "Implementation of Directive 2014/34/EU on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres".

- Legislative Decree no. 86 of 19 May 2016 - "Implementation of Directive 2014/35/EU on the harmonisation of the laws of Member States relating to the making available on the market of electrical equipment designed for use within certain voltage limits".

- Legislative Decree no. 128 of 22 June 2016 – "Implementation of Directive 2014/53/EU on the harmonisation of the laws of Member States relating to the making available on the market of radio equipment, repealing Directive 1999/5/EC”.

- Legislative Decree no. 194 of 06 November 2007, as amended. - "Implementation of Directive 2004/108/EC on electromagnetic compatibility, and Directive 2014/30/EU of 26 February 2014 on the harmonisation of the laws of the Member States relating to electromagnetic compatibility (recast) providing for its repeal".

- Legislative Decree no. 49 of 14 March 2014, as amended. – "Implementation of Directive 2012/19/EU on Waste from Electrical and Electronic Equipment (WEEE)".

- Legislative Decree no. 27 of 04 March 2014, as amended. – "Implementation of Directive 2011/65/EU on the restriction of the use of certain hazardous substances in electrical and electronic equipment".

- Legislative Decree no. 93 of 25 February 2000, as amended. - "Implementation of Directive 97/23/EC on pressure equipment and Directive 2014/68/EU on the harmonisation of the laws of the Member States relating to the making available on the market of pressure equipment (recast), providing for its repeal".

- Legislative Decree No. 233 of 12 June 2003. "Implementation of Directive 1999/92/EC on minimum requirements for improving the safety and health protection of workers exposed to the risk of explosive atmospheres".

- Law no. 186 of 1 March 1968 - "Provisions concerning the production of materials, equipment, machinery, electrical and electronic installations and systems".

- Legislative Decree no. 81 of 09 April 2008, as amended. – “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”.

- Legislative Decree no. 206 of 06 September 2005, as amended. – “Consumer code pursuant to Article 7 of Law no. 229 of 29 July 2003”;

- Ministerial Decree of 16 April 2008 - “Technical regulations for the design, construction, testing, operation and supervision of works and distribution systems and direct lines for natural gas with a density not exceeding 0.8”.

- Decree no. 93 of 21 April 2017, as amended – "Regulations on the implementation of legislation on the control of measuring instruments in service and the supervision of measuring instruments in compliance with national and European regulations".

- Ministerial Decree of 26 June 1984 as amended – "Classification of reaction to fire and approval of materials for the purposes of fire prevention".

- Resolution of 22 October 2008 - ARG/gas 155/08, as amended. – "Guidelines for the commissioning of gas metering units, characterised by minimum functional requirements and with remote reading and remote management functions, for the redelivery points of natural gas distribution networks".

- UNI EN 593 “Industrial valves - Metal butterfly valves”.

- UNI 11354 - "Shut-off devices for gas distribution and/or transportation networks - Butterfly valves”.

- UNI 9734 “Shut-off devices for gas pipelines. Steel valves with ball obturator”.

- UNI 10619-1 – "Natural gas pressure regulating installations and/or metering systems operating with maximum upstream pressure of 12 bar for industrial and civil use – Part 1: Design, construction and testing - General considerations".

- UNI 10619-3 – "Natural gas pressure regulating installations and/or metering systems operating with maximum upstream pressure of 12 bar for industrial and civil use – Part 3: Design, Construction and Testing – Gas Metering Plants".

- UNI 10285 - "Monolithic insulation joints. 80 ≤ ND ≤ 600. NP 16".

- UNI EN 751-3 "Sealing material for metallic threaded joints in contact with 1st, 2nd and 3rd family gases and hot water - Unsintered PTFE tapes".

- UNI EN 1555-2 - “Plastic piping systems for the supply of gaseous fuels - Polyethylene (PE) - Part 2: Pipes”.

- UNI 11600 – "Operative instruction for periodic and random metrological inspections”.

- UNI EN 12732 "Gas infrastructures - Welding of steel pipework - Functional requirements".

- UNI EN 12327 "Gas infrastructures - Pressure testing, commissioning and decommissioning procedures for gas supply networks - Functional requirements".

- UNI EN 12405-1 "Gas meters - Conversion devices - Part 1: Volume conversion".

- UNI EN 13757-1 "Communication systems for meters – Data exchange".

- UNI EN ISO 15614-1 “Specification and qualification of welding procedures for metallic materials - Welding procedure test - Part 1: Arc and gas welding of steels and arc welding of nickel and nickel alloys”.

- UNI EN ISO 9606-1 “Qualification testing of welders - Fusion welding - Part 1: Steels”.

- UNI EN ISO 9712 "Non-destructive testing - Qualification and certification of non-destructive testing personnel - General principles".

- UNI EN ISO 17636-1 "Non-destructive testing of welds - Radiographic testing - Part 1: X and gamma-ray techniques with film".

- UNI EN ISO 10675-1 "Non-destructive testing of welds - Part 1: Radiographic testing of butt welds of steel, nickel, titanium and their alloys - Acceptance levels".

- UNI EN ISO 3452-1 "Non-destructive testing - Penetrant testing - Part 1: General Principles”.

- UNI EN ISO 23277 "Non-destructive testing of welds - Penetrant testing - Acceptance levels".

- UNI EN ISO 17638 "Non-destructive testing of welds - Magnetic particle testing".

- UNI EN ISO 23278 "Non-destructive testing of welds - Magnetic particle testing - Acceptance levels".

- UNI CEI EN ISO/IEC 17050-1 “Conformity assessment - Supplier's declaration of conformity. Part 1: General requirements”.

- UNI EN ISO 3183 – “Petroleum and natural gas industries - Steel pipe for pipeline transportation systems”.

- UNI EN 10226 “Pipe threads for thread seal coupling”.

- UNI/TS 11291-1 "Gas metering systems - Hourly-based gas metering systems - Part 1: General characteristics for remote reading or remote management system".

- UNI/TS 11291-2 "Gas metering systems - Hourly-based gas metering systems - Part 2: CTE Protocol".

- UNI/TS 11291-3 "Gas metering systems - Hourly-based gas metering systems - Part 3: CTR Protocol".

- UNI/TS 11291-4 "Gas metering systems - Hourly-based gas metering systems - Part 4: Requirements for meters with a capacity of more than 65 m3/h (meter >G40)".

- CEI EN 62305-1 (CEI 81-10/1) "Lightning protection. General Principles”.

- CEI EN 62305-2 (CEI 81-10/2) "Lightning protection. Risk assessment”.

- CEI EN 62305-3 (CEI 81-10/3) "Lightning protection. Material damage to structures and danger to people".

- CEI EN 62305-4 (CEI 81-10/4) "Lightning protection. Electrical and electronic installations in facilities".

- CEI EN 60079-0 "Explosive atmospheres. Part 0: Equipment - General Requirements".

- CEI EN 60079-11 "Explosive atmospheres. Part 11: Equipment with intrinsically safe protection mode "i"".

- CEI EN 60079-25 - "Explosive atmospheres. Part 25: Intrinsically safe electrical systems".

- CEI EN 60079-14 (CEI 31-33) – "Electrical apparatus for explosive gas atmospheres – Part 14: Electrical Installations in places with danger of explosion due to the presence of gas (other than mines)".

- CEI EN 61643-11 (IEC 37-8) – "Low-voltage surge protective devices – Part 11: Surge protective devices connected to low-voltage systems: Requirements and tests".

# Annex

- Annex 1 – T.S. 2401301“Turbine or Rotary Piston gas meters”.

- Annex 2 - Table M. 17850 "Steel dielectric joint, NP 16, butt-weld ends".

- Annex 3 – T.S. 1800300 “Polyethylene fittings and special parts”.

- Annex 4 – T.S. 15AA300 “Welded steel pipes for natural gas pipelines”.

- Annex 5 – S.T.V.F.C. 17AA300 “Steel fittings”.

- Annex 6 – T.S. 2000300 “Steel valves for gas pipelines”.

- Annex 7 – T.S. 9991300 - "Cartridge filter elements for filters of gas reduction and metering units and plants".

- Annex 8 – T.S. 23273. "List of pressure reducers-regulators approved for company use”.

- Annex 9 – T.S. 9991308 "Measuring and precision indicating instruments for plant installations".

# APPENDICES

- APPENDIX 1 -	“Sample declaration of conformity with this technical specification”

- APPENDIX 2 – “Sample declaration of exclusion from Directive 2014/34/EU”

- APPENDIX 3 – “Sample declaration of SOUND ENGINEERING PRACTICE (SEP)”

## Appendix 1

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN ISO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

(4)	The following products manufactured by us:

| Our material code (5) | Italgas Reti material code (6) |
| --- | --- |
| xxx |  |
| xxx | xxx |

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(7)	T.S. 2327331	Variable pressure metering unit for                Edition 3 of 26/04/2020

redelivery points of the gas network supplied with

upstream pressure between 0.15 and 5 bar

Additional information:

(8) 	...................................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(9) 	.............................................................			......................................................................................................................

(Name and position) 						(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- The “subject” must be unambiguously described so that the declaration of conformity can be referred to the subject in question.

- List all the products for which company use authorisation is being requested.

- For each individual product supplied, state the material code used by the Supplier.

- For each individual product supplied, please quote the material code assigned by Italgas, which can be found in the Italgas reference documents. If there are none, please contact SERTEC-NORM.

- Include references to the Italgas documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

## Appendix 2

ATEX Exclusion Declaration

We ..............................................................................................................................................................

(name of organisation)

with registered office in .............................................................................................................

(address)

as the .................................................................................................................................................

(Manufacturer / Authorised Representative)

declare under our sole responsibility that the products series

.....................................................................................................................................................................

.....................................................................................................................................................................

(name, type or model, batch, group or serial numbers)

described in the Technical Specification / document(s)

.....................................................................................................................................................................

.....................................................................................................................................................................

(when necessary)

to which this declaration refers, comply with the following legislative / regulatory document(s)

.....................................................................................................................................................................

.....................................................................................................................................................................

(title(s) and/or number(s) and date(s) of publication of the standard(s) or other legislative and/or regulatory document(s))

and, according to Article 1, subsection 1a) of Directive 2014/34/EU of 26 February 2014 (Legislative Decree no. 85 of 19 May 2016) and Chapter 1 of ATEX 2014/34/EU GUIDELINES (first edition), based on an ATEX analysis (see subsection 32 of the aforementioned ATEX 2014/34/EU GUIDELINES), do not fall within the scope of the Directive 2014/34/EU, as they do not risk causing an explosion due to the lack of potential ignition sources, as defined in Standard UNI EN 1127-1, when used in systems that comply with the following legislative and/or regulatory documents

.....................................................................................................................................................................

.....................................................................................................................................................................

.....................................................................................................................................................................

(title and/or number and date of publication of legislative and/or regulatory documents)

They can therefore be installed in all types of zones as defined in Legislative Decree no. 81 of 9 April 2008, as amended, Title XI (Directive 1999/92/EC of 16 December 1999).

.................................................................. 		..................................................................................................................................

(place and date of issue)		(name and signature or equivalent stamp of authorised person)

## Appendix 3

Declaration of falling within Article 3, subsection 3 of Legislative Decree no. 93

(SEP Declaration)

We ..............................................................................................................................................................

(name of organisation)

with registered office in .............................................................................................................

(address)

as the .................................................................................................................................................

(Manufacturer / Authorised Representative)

we declare that, following the analysis carried out in accordance with Legislative Decree no. 26 of 15 February 2016 implementing the Integration Directive 2014/68/EU, the series products:

..................................................................................................................................................................... ..................................................................................................................................................................... (name, type or model, batch, group or serial number)

described in the document:

…………………..………..……………………………………………………………………………….

…………………..………..……………………………………………………………………………….

(title and/or number and date of publication of the Standard(s) or other regulatory document(s))

to which this declaration refers, fall under Article 3, subsection 3 of Legislative Decree no. 93 of 25 February 2000 as amended, and are therefore subject to the provisions thereof. Consequently the products mentioned are not subject to CE marking for the application of Legislative Decree no. 93 of 25 February 2000 as amended.

Henceforth, only the acronym "VPMU" will be used, as there is no difference in flow rates between interruptible and non-interruptible Units, for both types of metering units with the exclusion of Table1 showing the material codes of the same.

Supplier means the party responsible for the design and construction of the products or its legal representative as defined in Legislative Decree no. 206 of 6 September 2005 as amended and supplemented. - "Consumer code, pursuant to Article 7 of Law no. 229 of 29 July 2003."

DESTINATION UNIT means the OPERATIONAL UNIT receiving the VPMU.

Only the metering part.

SOUND ENGINEERING PRACTICE.