“TECHNICAL SPECIFICATION FOR EVALUATION”

S.T.V. 9992320

ODOURISATION SYSTEM

| Compiled by | CORID | FERRACUTI, GIOVANNI |
| --- | --- | --- |
| Compiled by | SERTEC-NORM | GOZZANI, RICCARDO |
| Verified | SERTEC-NORM | VARESE, ENRICO |
| Checked by | PROMA/CMMAT | FASSINO, SILVIO |
| Checked by | HSEQ | BOLZONI, GIANLUCA |
| Approved by | SERTEC | COMAZZI MARCO |

SUMMARY

1	PRELIMINARY INFORMATION	5

1.1	Cancels and replaces	5

1.2	Reason for issue	5

1.3	Definitions	6

2	PURPOSE AND FIELD OF APPLICATION	6

2.1	Purpose	6

2.2	Field of application	6

3	SPECIFICATIONS	6

4	TECHNICAL CHARACTERISTICS	6

4.1	Plant types	7

4.1.1	Odourisation injection plants	7

4.1.1.1	Schematic diagram and main components of the odourisation injection plant and back-up plant with lapping drum by-pass:	7

4.1.1.2	Schematic diagram and main components of the odourisation injection plant and back-up plant with lapping drum by-pass, with one or (max) two service tanks:	8

4.1.1.3	Schematic diagram and main components of the "Primary odourisation injection plant and injection back-up plant (master/slave) plus 2nd back-up plant with lapping drum by-pass, with one or (max) two service tanks of a total capacity of ≥ 1500 litres:	10

4.1.2	Back-up system with odourisation lapping drum by-pass	12

4.1.3	Filtration system for venting and/or purging gas odourisation plants	13

4.1.4	Schematic diagram and main components for setting up pre-assembled apparatus composed of: service tank(s), spill containment system and collection tank:	14

4.2	Sizing criteria of odourisation plants	14

4.3	Materials, pipes, joints and valves	15

4.4	Protection against corrosion by external agents	15

4.5	Remote control and remote reading on odourisation plants	16

4.5.1	Remotely controlled values on odourisation plants:	16

4.5.2	Remote reading on odourisation plants:	16

4.5.3	Operating logic of remote alarms on odourisation plants:	16

4.6	Pressure equipment	17

4.7	Electrical and electronic systems serving the odourisation plants	18

4.8	Earthing and lightning protection systems	18

4.9	Containment system	18

4.10	Technical assessment	19

5	DOCUMENTATION REQUIRED FROM THE SUPPLIER	19

5.1	Supplier()	19

5.2	Documentation for the company approval process	19

5.3	Marking and labelling	19

5.4	Test Documentation	19

5.5	Documentation accompanying the supply	20

6	TESTS AND INSPECTIONS	20

6.1	Type tests	20

6.2	Tests and inspections	21

6.3	Visual and dimensional inspection	21

6.4	Mechanical strength test	21

6.4.1	Main gas circuit	21

6.4.2	Dosing drum and Service tank	22

6.5	Leak test	22

6.6	Non-Destructive Testing (NDT) of welds	22

6.7	Right of the Client	22

7	REFERENCE STANDARDS	23

8	APPENDICES	24

8.1	APPENDIX 1 – "Standard connection plate for odorant refilling"	24

8.2	APPENDIX 2 – "Connection system for bulk odorant refilling from tanker truck"	24

8.3	APPENDIX 3 – "Magnetic and magnetostrictive indicator of odorant levels"	24

8.4	APPENDIX 4 – “Sample declaration of conformity with this technical specification”	24

8.5	APPENDIX 5 – "ATEX Exclusion Declaration (for tanks and drums)".	24

9	annexes	24

9.1	Annex 1: "Functional diagram of injection odourisation plant and back-up lapping by-pass”.	24

9.2	Annex 2: "Functional diagram of injection odourisation plant and back-up lapping by-pass with service tank”.	24

9.3	Annex 3: "Functional diagram of injection odourisation plant and injection back-up plant and 2nd lapping by-pass back-up system".	24

9.4	Annex 4: "Schematic diagram of pre-assembled apparatus with service tank, spill containment system and collection tank".	24

9.5	Annex 5: "Schematic diagram of pre-assembled apparatus with two service tanks, spill containment system and collection tank".	24

9.6	Annex 6: S.T.V.F.C. 9992322 "Filter systems for odourisation plants".	24

Appendix 1	25

Appendix 2	27

Appendix 3	29

Appendix 4	30

Appendix 5	31

# PRELIMINARY INFORMATION

## Cancels and replaces

This specification cancels and replaces T.S. 9992320 Edition 4 dated 15/06/2017 "ODOURISATION PLANTS" issued by SERTEC-NORM on 15/06/2017.

## Reason for issue

Updating of T.S. 9992320 Edition 4 became necessary due to:

- Changed legislative context;

- Issuing of new national and European standards (e.g. UNI, CEI, EN, etc.)

- Update of Appendix 1 "Connection plate for external refilling":

  - for refilling with odorant prepared in drums.

  - for refilling with bulk odorant from a tanker truck.

- Update of Annex 1 "Primary odourisation injection plant and back-up plant with lapping drum by-pass”.

- Update of Annex 2 ''Primary odourisation injection plant and back-up plant with lapping drum by-pass, with one or (max) two service tanks".

- Update of Annex 3 "'Primary odourisation injection plant and injection back-up plant (master/slave) plus 2nd back-up plant with lapping drum by-pass, with one or (max) two service tanks".

- Addition of Annex 4 "Schematic diagram of pre-assembled apparatus with service tank, spill containment system and collection tank".

- Addition of Annex 5 "Schematic diagram of pre-assembled apparatus with two service tanks, spill containment system and collection tank".

## Definitions

The technical definitions contained in this specification conform to those of the standards listed in point 7 “Reference standards”.

# PURPOSE AND FIELD OF APPLICATION

## Purpose

The purpose of this Technical Specification is to define:

- the design and installation criteria for odourisation plants, as well as material characteristics and reference standards;

- functional plant diagrams and application methods to correctly dose the required amount of odorant into the gas flow delivered to the user.

## Field of application

This T.S. applies whenever the opportunity arises:

- to approve for company use new products concerning the "odourisation injection plants" described in this T.S. and manufactured by a potential new Supplier or an existing Supplier;

- retrofit existing odourisation plants using the technical indications of this T.S.

# SPECIFICATIONS

- This specification must be understood as an integral part of the “ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS RETI.”

- This specification contains the minimum technical requirements demanded by Italgas Reti based on the reference Legislative and Technical Standards.

- It is the Supplier's responsibility to ensure that the products supplied fully comply with the provisions of this technical specification. If the materials in question are supplied by an installer, the installer must document their compliance.

- It is the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. sharp edges or incorrect directions for use and maintenance), which may jeopardise the health and safety of the Client's workers in relation to the provisions of Italian Legislative Decree no. 81/08, as amended and supplemented.

- For any technical and operational aspects that conflict with or are not mentioned in this T.S. but that nevertheless pertain to the design, installation, maintenance and use of the products, it is the Supplier's responsibility to refer to the legislation and regulations in force.

- The odourisation plants must include all the necessary measures to avoid any pressure transfer from upstream to downstream.

# TECHNICAL CHARACTERISTICS

Combustible gases for domestic or similar use, distributed via pipes, must have a characteristic odour intensity sufficient for their presence to be perceptible to the user before the danger threshold is reached.

An odourisation plant is composed of equipment and accessories suitable for injecting and dosing the right amount of odorant based on the gas flow to be odourised according to predetermined ratios.

The odourisation plant can be installed downstream of withdrawal, reduction and metering plants, at reduction and/or metering plants in general or along natural gas distribution networks.

The odourisation plants must be designed, constructed and commissioned in accordance with the requirements of the UNI 9463 standard "Odourisation plants and odorant deposits for combustible gases used in domestic or similar applications". For anything not expressly provided for in this T.S., reference must be made to the aforementioned technical standard, as well as to the other legislative and regulatory provisions in force on the matter, a non-exhaustive list of which is given under 7 "Reference standards".

Unless explicitly referred to otherwise, the regulations cited in this T.S. are to be understood as the latest published edition, inclusive of any subsequent amendments/updates and/or corrigenda; the legislative provisions are to be considered inclusive of any subsequent amendments and additions.

## Plant types

The primary odourisation plants, covered by this T.S., are of the injection type.

In particular, considering that at least one back-up plant must always be provided, any one of the following plant solutions may be provided:

- Primary odourisation injection plant and back-up plant with lapping drum by-pass.

- Primary odourisation injection plant and back-up plant with lapping drum by-pass, with one or (max) two service tanks.

- Primary odourisation injection plant and injection back-up plant (master/slave) plus 2nd back-up plant (not mandatory by law) with lapping drum by-pass, with one or (max) two service tanks.

The choice of the type of odourisation plant is made, on a case-by-case basis, depending on the technical characteristics of the distribution plant it serves and is aimed at optimising management of plant operations.

### Odourisation injection plants

Odourisation injection plants are used to nebulise the odorant in the dosed quantity, directly into the gas to be odourised, by means of a dosing system.

Odourisation injection plants must be supplied by the manufacturers qualified by Italgas Reti and approved for company use listed in the Appendix to Annex 1 of Italgas Reti Instruction ITG-IOP-092.

#### Schematic diagram and main components of the odourisation injection plant and back-up plant with lapping drum by-pass:

are shown in Annex 1. The plant consists primarily of:

- A control and regulation system: acquires flow rate data from the computerised gas volume measurement system, controlling the electromechanical devices of the odourisation plant so as to ensure that the quantities of odorant introduced comply with the set concentration. It must have the following characteristics:

  - be suitable for placing inside an enclosure with an IP55 or higher degree of protection;

  - be suitable for installation in a "non-hazardous location";

  - be suitable for being electrically powered with 230 VAC (50 Hz) or 24/12 VDC;

  - be able to store, for at least one month, data on the volume of gas dispensed, the quantity of odorant fed into the system, and the daily diagnostics of the system provided in TXT format via a standard RS-232 serial port.

  - be table to exclude, during regular operation of the injection system, the passage of the gas to be odourised into the lapping drum (back-up system), by closing one of the bypass branches (in special cases both), actuating the "positive safety" lapping exclusion valve.

  - be able to reactivate the passage of the gas to be odourised in the lapping drum in the event of a malfunction in the operation of the primary system.

- Injection system: this must be designed and constructed in such a way as to favour maximum nebulisation of the odorant liquid into the gas flow to be odourised and easy disassembly of the parts, thus facilitating maintenance operations.

The injection system must be fitted with a data plate which cannot be removed or altered, placed in a clearly visible position, bearing at least the following information:

  - company name of the manufacturer;

  - serial number and year of construction;

  - minimum and maximum odorant dispensing limits expressed in L/h;

  - maximum permissible pressure at the injection point;

  - usable odorant(s).

- Back-up odourisation system: this consists of a system with a lapping drum by-pass, which is activated automatically in the event of a malfunction of the primary injection odourisation system.

  - Lapping drum: in this plant configuration, without additional tanks, it (also) has the function of containing the odorant which the injection system is directly supplied by. For existing plants only, the use of quality steel drums in compliance with UNI EN 10028 or equivalent (sulphur-prevalent odorants) is permitted, while for new constructions or replacements on existing plants, the use of stainless steel drums with characteristics no less than X5 Cr Ni 18/10, in compliance with UNI EN 10028-7 (mercaptan-prevalent odorants) is required. The indicative capacities that can be used are 25, 75, 125, 250, 490 litres.

  - The dosing drum must be equipped with: see description under 4.1.2.

  - The installation of the dosing drum must have a slope of 3% from the horizontal plane in the direction of the drainage valve.

N.B. Odourisation plants with a total capacity of up to 25 litres (small plants) (Standard UNI 9463-2 point 4.4.1) must consist of a single tank (drum) and may not be equipped with a service tank.

#### Schematic diagram and main components of the odourisation injection plant and back-up plant with lapping drum by-pass, with one or (max) two service tanks:

are shown in Annex 2. The plant consists primarily of:

- A control and regulation system: acquires flow rate data from the computerised gas volume measurement system, controlling the electromechanical devices of the odourisation plant so as to ensure that the quantities of odorant introduced comply with the set concentration. It must have the following characteristics:

  - be suitable for placing inside an enclosure with an IP55 or higher degree of protection;

  - be suitable for installation in a "non-hazardous location";

  - be suitable for being electrically powered with 230 VAC (50 Hz) or 24/12 VDC;

  - be able to store for at least one month, data on the volume of gas dispensed, the quantity of odorant fed into the system, and the daily diagnostics of the system provided in TXT format via a standard RS-232 serial port;

  - be table to exclude, during regular operation of the injection system, the passage of the gas to be odourised into the lapping drum (back-up system), by closing one of the bypass branches (in special cases both), actuating the "positive safety" lapping exclusion;

  - be able to reactivate the passage of the gas to be odourised in the lapping drum in the event of a malfunction in the operation of the primary system;

- Injection system: this must be designed and constructed in such a way as to favour maximum nebulisation of the odorant liquid into the gas flow to be odourised and easy disassembly of the parts, thus facilitating maintenance operations.

The injection system must be fitted with a data plate which cannot be removed or altered, placed in a clearly visible position, bearing at least the following information:

  - company name of the manufacturer;

  - serial number and year of construction;

  - minimum and maximum odorant dispensing limits expressed in L/h;

  - maximum permissible pressure at the injection point;

  - usable odorant(s).

- Back-up odourisation system: this consists of a system with a lapping drum by-pass, which is activated automatically in the event of a malfunction of the primary injection odourisation system.

- Service tank (single or, where necessary, a maximum of two), with the function of containing the odorant, from which the injection system is directly supplied. For existing plants only, the use of quality steel tanks in compliance with UNI EN 10028 or equivalent (sulphur-prevalent odorants) is permitted, while for new constructions or replacements on existing plants, the use of stainless steel tanks with characteristics no less than X5 Cr Ni 18/10, in compliance with UNI EN 10028-7 (mercaptan-prevalent odorants) is required. The indicative capacities that can be used per individual tank are 250, 365, 1,350, 1,500 litres.

- The service tank must be equipped with:

  - vertical level with magnetic float actuating the reading indicator placed in a vertical transparent tube with a graduated scale, for the precise display of the odorant level in the service tank;

  - magnetostrictive level sensor, installed in the tank or connected to the vertical magnetic float level indicator, always placed in a vertical position, compliant with ATEX ADI 4÷20 mA, with a minimum measurement accuracy class of 0.025 %, equipped with a correction in litres of odorant present in the service tank and connected via TLC to the Company supervision system (today COPT);

  - odorant loading connection fitted with a leak-proof shut-off valve on both stem and seat;

  - tank depressurisation and vent connection fitted with a leak-proof shut-off valve on both stem and seat;

  - pressure intake with control pressure gauge;

  - bottom drainage connection equipped with a leak-proof shut-off valve on both stem and seat. The valve must be equipped with a blind cap or flange closing device to avoid the risk of odorant leakage in the event of an operating error;

  - odorant uptake connection for injection dosing system, equipped with a leak-proof shut-off valve on both the stem and the seat, made with tubing that returns into the dosing drum of a length of at least 5% of its nominal diameter;

  - The installation of the service tank must have a slope of 3% from the horizontal plane in the direction of the drainage valve.

- Back-up system: the dosing drum is used to contain the odorant, thereby allowing odourisation by lapping of the gas flow with the odorant. For existing plants, the use of quality steel drums in compliance with UNI EN 10028 or equivalent (sulphur-prevalent odorants) is permitted, while for new constructions or replacements on existing plants, the use of stainless steel drums with characteristics no less than X5 Cr Ni 18/10, in compliance with UNI EN 10028-7 (mercaptan-prevalent odorants) is required. The indicative capacities that can be used are, 125, 250, 365 litres.

- The dosing drum must be equipped with: see description under 4.1.2.

- The installation of the dosing drum must have a slope of 3% from the horizontal plane in the direction of the drainage valve.

#### Schematic diagram and main components of the "Primary odourisation injection plant and injection back-up plant (master/slave) plus 2nd back-up plant with lapping drum by-pass, with one or (max) two service tanks of a total capacity of ≥ 1500 litres:

are shown in Annex 3. The plant consists primarily of:

- Two control and regulation systems, completely separate and independent (usually the same, one of which active and the other in stand-by): they acquire flow rate data from the computerised gas volume measurement system, each separately controlling the electromechanical device connected to the odourisation plant so as to ensure that the quantities of odorant introduced comply with the set concentration. These must have the following characteristics:

  - be suitable for placing inside an enclosure with an IP55 or higher degree of protection;

  - be suitable for installation in a "non-hazardous location";

  - be suitable for being electrically powered with 230 VAC (50 Hz) or 24/12 VDC;

  - each of the two systems must have sufficient back-up batteries to ensure complete operation of the injection for a period of at least three hours;

  - both systems must be able to store, for at least one month, information on the volume of gas dispensed, the quantity of odorant fed into the system, and the daily diagnostics of the plant provided in TXT format via a standard RS-232 serial port;

  - both systems must be able to exclude each other, during regular operation, as well as to exclude the passage of the gas to be odourised into the lapping drum (back-up system), by closing one of the bypass branches (in special cases both), actuating the "positive safety" lapping exclusion valve;

  - both systems must mutually be capable of activating the one in stand-by (1st back-up system), when there is a fault in the injection system in service;

  - both systems must be able to reactivate the passage of the gas to be odourised in the lapping drum (2nd back-up system) in the event of a malfunction in both injection plants.

- Two injection systems: completely separate and independent (usually the same, one of which active and the other in stand-by) which must be designed and constructed in such a way as to favour maximum nebulisation of the odorant liquid into the gas flow to be odourised and easy disassembly of the parts, thus facilitating maintenance operations.

The injection system must be fitted with a data plate which cannot be removed or altered, placed in a clearly visible position, bearing at least the following information:

  - company name of the manufacturer;

  - serial number and year of construction;

  - minimum and maximum odorant dispensing limits expressed in L/h;

  - maximum permissible pressure at the injection point;

  - usable odorant(s).

- 2nd back-up odourisation system: this consists of a system with a lapping drum by-pass, which is activated automatically in the event of a failure of both primary injection odourisation systems.

- Service tank (single, or, where necessary, a maximum of two), with the function of containing the odorant, from which the injection system is directly supplied. For existing plants only, the use of quality steel tanks in compliance with UNI EN 10028 or equivalent (sulphur-prevalent odorants) is permitted, while for new constructions or replacements on existing plants, the use of stainless steel tanks with characteristics no less than X5 Cr Ni 18/10, in compliance with UNI EN 10028-7 (mercaptan-prevalent odorants) is required. The indicative capacities per individual tank are 250, 365, 1,350 and 1,500 litres. In addition, with appropriate reference to the size of the WRMP, (it is permissible to have service tank(s) with a total capacity of approximately one year's odorant consumption), of suitable capacity up to a maximum of 2,950 litres each tank.

- The service tank must be equipped with:

  - vertical level with magnetic float actuating the reading indicator placed in a vertical transparent tube with a graduated scale, for the precise display of the odorant level in the service tank;

  - magnetostrictive level sensor, installed in the tank or connected to the vertical magnetic float level indicator, always placed in a vertical position, compliant with ATEX ADI 4÷20 mA, with a minimum measurement accuracy class of 0.025 %, equipped with a correction in litres of odorant present in the service tank and connected via TLC to the Company supervision system (today COPT);

  - odorant loading connection fitted with a leak-proof shut-off valve on both stem and seat;

  - tank depressurisation and vent connection fitted with a leak-proof shut-off valve on both stem and seat;

  - pressure intake with control pressure gauge;

  - bottom drainage connection equipped with a leak-proof shut-off valve on both stem and seat. The valve must be equipped with a blind cap or flange closing device to avoid the risk of odorant leakage in the event of an operating error;

  - odorant uptake connection for injection dosing system, equipped with a leak-proof shut-off valve on both the stem and the seat, made with tubing that returns into the dosing drum of a length of at least 5% of its nominal diameter.

  - the installation of the service tank must have a slope of 3% from the horizontal plane in the direction of the drainage valve.

N.B. The service tanks in Annex 3, on account of the normally large capacity, can also be filled with bulk odorant from tanker trucks, Appendix 2 of this T.S. shows the connection required. In addition, to enable filling, a three-phase 380V FM socket must be installed in a safe area to operate the tanker truck's unloading pump.

- 2nd back-up system composed of: dosing drum used to contain the odorant, thereby allowing odourisation by lapping of the gas flow with the odorant. For existing plants, the use of quality steel drums in compliance with UNI EN 10028 or equivalent (sulphur-prevalent odorants) is permitted, while for new constructions or replacements on existing plants, the use of stainless steel drum with characteristics no less than X5 Cr Ni 18/10, in compliance with UNI EN 10028-7 (mercaptan-prevalent odorants) is required. The indicative applicable capacities are 125, 250, 365 litres.

- The dosing drum must be equipped with: see description under 4.1.2.

- The installation of the dosing drum must have a slope of 3% from the horizontal plane in the direction of the drainage valve.

### Back-up system with odourisation lapping drum by-pass

Only back-up plants with a by-pass into which part of the gas in transit on the main pipe is forced to flow inside a dosing drum containing odorant are permitted for company use for lapping odourisation. Full-flow lapping plants are therefore not permitted.

The back-up systems, with by-pass odourisation drums, are schematically illustrated in Annexes 1, 2 and 3 and consist of the following components:

- Δp generator: located on the main pipe, it enables the creation of the pressure difference that forces part of the gas (bypass flow) to flow into the dosing drum. It consists of a butterfly valve, equipped with a stress reducer (with control and adjustment handwheel), having a free through cross-section in the fully closed position equal to at least 5% of the cross-section of the pipe it is installed on.

- Regulating valve: allows precision regulation of the gas flow passing through the by-pass; it consists of a needle valve with micrometric opening reference.

- Dosing drum: this is used to contain the odorant, thereby allowing odourisation by lapping of the gas flow with the odorant. For existing plants, the use of quality steel drums in compliance with UNI EN 10028 or equivalent (sulphur-prevalent odorants) is permitted, while for new constructions or replacements on existing plants, the use of stainless steel drums with characteristics no less than X5 Cr Ni 18/10, in compliance with UNI EN 10028-7 (mercaptan-prevalent odorants) is required. The indicative capacities are 25, 75, 125, 250, 365 and 490 litres.

N.B.: Odourisation plants with a total capacity of up to 25 litres (small plants) (Standard UNI 9463-2 point 4.4.1) must consist of a single tank (drum) and may not be equipped with a service tank.

The installation of the dosing drum must have a slope of 3% from the horizontal plane in the direction of the drainage valve.

- The dosing drum must be equipped with:

  - vertical level with magnetic float actuating the reading indicator placed in a vertical transparent tube with a graduated scale, for the precise display of the odorant level in the dosing drum;

  - magnetostrictive level sensor, installed in the drum or connected to the vertical magnetic float level indicator, always placed in a vertical position, compliant with ATEX ADI 4÷20 mA, with a minimum measurement accuracy class of 0.025 %, equipped with a correction in litres of odorant present in the dosing drum and connected via TLC to the Company supervision system (today COPT);

  - odorant loading connection equipped with a leak-proof shut-off valve on both stem and seat.

  - drum depressurisation and vent connection equipped with a leak-proof shut-off valve on both stem and seat;

  - pressure intake with control pressure gauge.

  - bottom drainage connection equipped with a leak-proof shut-off valve on both stem and seat. The valve must be equipped with a blind cap or flange closing device to avoid the risk of odorant leakage in the event of an operating error;

  - odourisation injection plant uptake connection, made with tubing that returns into the dosing drum of a length of at least 5% of its nominal diameter;

  - shut-off valves on the flow connections from the gas line bypass to the dosing drum;

### Filtration system for venting and/or purging gas odourisation plants

The function is to filter the gas saturated with odorant vapours coming from the depressurisation step of the dosing drum and/or the service tank(s) when transferring odorant from one tank to another.

Also when bulk odorant refilling from tanker trucks is envisaged and carried out, our WRMP filtration system will be used during refilling operations.

If, instead, odorant refilling is carried out by the Supplier with product in drums, the purification of the vent gases must be carried out by the Supplier, who bears the corresponding contractual burden.

Only in the event that the odourisation system does not comply with the diagrams attached to this specification and it is not possible for the odorant supplier to recover the vent gases for purification, will the WRMP filtration systems be used.

The filtering function is performed by making the flow of odourised gas pass through the system, which consists of a special container containing activated carbon, where the odorant molecules are withheld, rendering the gas odourless for subsequent expulsion into the atmosphere.

- The dimensions of the filter to be provided for the plant layout in Annex 1 must be suitable for containing at least 6 kg of activated carbon.

- The dimensions of the filter to be provided for the plant layout in Annex 2 must be suitable for containing at least 12 kg of activated carbon.

- The dimensions of the filter to be provided for the plant layout in Annex 3 must be suitable for containing at least 50 kg of activated carbon.

Note: Activated carbon is normally marketed in 25 kg packages.

They can also be applied/used, where necessary, on other plants such as VPMUs and IRPs, where an odourisation system may be present. Filter characteristics are given in the T.S. 9992322.

### Schematic diagram and main components for setting up pre-assembled apparatus composed of: service tank(s), spill containment system and collection tank:

are shown in Annexes 4 and 5.

In order to cope with the increased gas flow and provide adequate odorant capacity, on numerous WRMPs of the Italgas Reti fleet (today about 20), again referring to the UNI 9463:2012 standard, the volume of the service tanks needs to be increased, exceeding the overall limit of 500 litres per WRMP, but remaining within 3,000 litres.

  - Annex 4 describes the structural layout with a 1,500-litre service tank resting on load-bearing saddles on the ground, a raised walking surface with an integrated containment system (tank) for any spills and collection tank underneath supported on the ground.

The structure described can be housed in the (ATEX) room in the WRMP or, if there is insufficient space, outside the WRMP on a flat concrete structure housed in a suitable stainless steel metal cabinet.

  - Annex 5 describes the structural layout with two 1,350-litre service tanks resting on load-bearing saddles on the ground, a raised walking surface with an integrated containment system (tank) for any spills and collection tank underneath supported on the ground.

The structure described can be housed in the (ATEX) room in the WRMP or, if there is insufficient space, outside the WRMP on a flat concrete structure housed in a suitable stainless steel metal cabinet.

## Sizing criteria of odourisation plants

The system must be sized to ensure that the gas injected into the distribution network is sufficiently odourised to comply with the legal requirements in force and to maintain, as far as possible, a constant odour concentration in the gas injected into the network.

In particular, the following table shows the minimum performance requirements with reference to the odourisation plants listed in point 4.1.

Table 1

|  | Plant type |  |
| --- | --- | --- |
|  | Lapping | Injection |
| Calibration range | 0 - 80 mg/Sm³ | 0 - 100 mg/Sm³ |
| Sensitivity | 5 mg/Sm³ | 1 mg/Sm³ |
| Accuracy | ± 15 % | ± 5 % |
| Precision | ± 5 % | ± 5 % |

Calibration range: range of odorant concentration values that can be delivered by the system.

Sensitivity: minimum variation that the system can generate with regard to the desired concentration setting (for injection this value can be defined through the smallest value that can be set via the control panel, for lapping through the smallest needle valve variation).

Accuracy: an index expressing how closely the set concentration value is aligned with the actual value delivered by the odourisation plant; it is determined as the difference between the ideal value and the average of a series of 5 values. These values are determined through five tests in which the external conditions are kept constant (flow to be odourised, concentration setting, etc.).

Precision: index of repeatability of odorant concentration (basically indicates stability of delivery). It is determined as the coefficient of variation (mean/standard deviation) of a series of five tests; these tests involve a procedure similar to that described for accuracy.

## Materials, pipes, joints and valves

All parts of the plant must be made of strong and durable materials, taking into account the chemical action of odorants.

In particular, fixed containers, dosing systems and fixed connections must be made of:

- quality steel complying with the relevant parts of the UNI EN 10028 series of standards, for all sulphur-prevalent odorants;

or:

- stainless steel with properties not less than X5 Cr Ni 18/10 in accordance with UNI EN 10028-7, for mercaptan-prevalent odorants,

and must prevent, as far as possible, the stagnation of the odorant.

For mobile connections, chloroprene rubbers, stainless steel hoses and hoses made of PTFE or similar should be used, suitably protected from external mechanical actions.

The connections between the various parts of the odourisation plant must be made with rigid metal pipes, bending of which is permitted as long as their mechanical resistance is guaranteed. The connecting joints of the pipes must be designed and manufactured in such a way as to guarantee a perfect seal over time, even in the presence of mechanical stresses to which the systems may be subjected. Joints between rigid metal pipes must be made by welding, those between pipes and shut-off devices or other equipment must be made by conical threading or by flanges fitted with gaskets resistant to the action of the odorant liquid. These joints must be made according to the manufacturer's instructions and the relevant standards.

Shut-off valves are of the ball type, conforming with UNI 9734 and equipped with flanged connections.

All the materials constituting the odourisation system as a whole must have a minimum strength class of NP 16 / ANSI 150 and operate correctly in a temperature range of -10 °C to +50 °C.

## Protection against corrosion by external agents

- Non-stainless steel fixed containers and rigid connections must be painted externally with a paint cycle suitable for an industrial environment, having, as a minimum, the following characteristics:

- High coefficient of adhesion to the surface to be protected;

- Good anti-corrosion properties;

- Reduced porosity and permeability to gases and liquids;

- Resistance to the persistent action of atmospheric and chemical agents.

- An example of a painting cycle is as follows:

- Primer: zinc-based product;

- Top coat: polyurethane-based paint.

## Remote control and remote reading on odourisation plants

The analogue (4 - 20 mA) or digital (on/off) electrical signals of the odourisation plants must be connected to the RTUs of the reduction plant and transmitted from them to the Company's remote control and remote reading system (today "COPT"), so as to remotely detect the status of the equipment functions and measured values.

The transducers and their connection circuits to the RTU must be manufactured according to the requirements of CEI EN 60079-14.

### Remotely controlled values on odourisation plants:

- OPA (odourisation plant alarm) is the digital signal (on/off) expressing the status of the injection dosing unit:

  - "ok" = plant operating regularly.

  - "alarm" or "signal" = plant with functional fault.

- LIO (lapping in operation) is the digital signal (on/off) expressing the status of the by-pass exclusion valve(s) from the lapping drum:

  - "off" = lapping off (injection dosing unit regularly in operation).

  - "on" = lapping on (injection dosing unit stopped due to fault).

### Remote reading on odourisation plants:

- OC (odour content) is the analogue value, transmitted by the injection dispenser, expressing the amount of odorant in mg/cubic metre of transited gas.

- OL (odorant level) is the analogue value transmitted by the magnetostrictive level(s), one level on each individual odorant container, whether service tanks or lapping drums.

### Operating logic of remote alarms on odourisation plants:

- Following signals from the RTUs installed in the WRMPs, COPT (currently) must transmit an alarm signal to the on-call personnel, whatever the time or day, if the following conditions occur simultaneously on the plants in Annexes 1 and 2:

  - The OPA signal is present, indicating that the injection dosing unit has stopped working due to a fault or possibly lack of electricity, and the back-up battery is not present or is flat.

  - The LIO "OFF" signal is still on, indicating that the automatic lapping back-up system has not been activated.

In the case described in practice, the odourisation plant has stopped odourising the gas being injected into the network, and it is necessary to intervene as quickly as possible in order to re-establish the correct gas odourisation conditions.

- Following signals from the RTUs installed in the WRMPs, COPT (currently) must transmit an alarm signal to the on-call personnel, whatever the time or day, if the following conditions occur simultaneously on the plants in Annex 3:

  - The OPA signals on both injection dosing devices is present at the same time, even in the possible presence of the LIO "ON" signal confirming activation of the 2nd lapping back-up system.

N.B. Where there are two injection dosing devices, one back-up to the other, (diagram Annex 3), the WRMPs are of considerable size, with significant flows and strong variations in flow, as a result in the simultaneous presence of both OPA signals, an alarm signal must be transmitted, even in the possible presence of LIO "ON" of the 2nd back-up system, since the latter has a fixed calibration and cannot guarantee stable odourisation.

- COPT (currently) must instead transmit during working hours, an extraordinary maintenance request, possibly conveyed via WFM, if the following conditions occur on the plants listed in the diagrams in Annexes 1, 2 and 3:

  - OPA signal from the injection dosing unit is present

  - The LIO signal changes from "OFF" to "ON", thus proving the automatic activation of the back-up lapping system.

  - For the plants shown in the diagram in Annex 3, this condition must occur for the presence of the OPA signal on one of the two injection dosing devices.

N.B. in the case described above, the plant is odourising via the back-up plant and it is advisable to carry out the necessary maintenance to reset the malfunctioning injection dosing device as quickly as possible, but during working hours.

The analogue (with 4 - 20 mA outputs) or digital electrical signals of the odourisation plants must be connected to the RTUs of the WRMP in order to be managed by Italgas Reti. The transducers and their connection circuits to the RTU must be manufactured according to the requirements of CEI EN 60079-14.

## Pressure equipment

Pressure equipment intended to contain the odorant, such as drums and service tanks, must meet the requirements of Legislative Decree no. 26 of 15 February 2016 implementing Integration Directive 2014/68/EU on the harmonisation of the laws of the Member States relating to the making available on the market of pressure equipment.

They must:

- meet the essential safety requirements set out in Annex 1 of the aforementioned Decree;

- be CE marked on the containers in a legible and indelible manner.

In addition, each container or tank must be marked with at least the following information:

- company name of the manufacturer;

- year of construction;

- identification of pressure equipment according to its nature:

- type, serial or lot identification number

- factory number;

- maximum allowed pressure (AP), in kilopascals (or in bar);

- minimum/maximum permissible temperature (TS);

- volume V expressed in litres;

and a label indicating:

- the trade name of the odorant and the reference to the international classification system (UN number);

- the relevant hazard marking;

- the word "odorant".

## Electrical and electronic systems serving the odourisation plants

Electrical equipment intended for use in potentially explosive atmospheres, as defined in Legislative Decree no. 233/03 (Directive 1999/92/EC), must fall within the scope of Legislative Decree no. 85/2016 (Directive 2014/34/EU). The installation and wiring of electrical equipment suitable for ATEX zones must comply with the requirements of CEI EN 60079-14 and the standards referred to therein.

Any electrical equipment that is not suitable for the type of hazardous area must only be installed in a "safe area" (e.g. electrical room in WRMP buildings) and must in any case be suitable in terms of construction for the foreseeable environmental influences. In the transition between hazardous and non-hazardous locations, the requirements set out in CEI EN 60079-14 for the specific types of electrical constructions to be used (e.g. locking fittings with sealing mixture) must be observed.

## Earthing and lightning protection systems

Odourisation plants must be protected against the effects of lightning in accordance with the requirements of the relevant technical standards (see CEI EN 62305-1÷4). The appropriate protective measures, if any, are identified for the individual plant in relation to the findings of the lightning risk assessment document prepared in accordance with CEI EN 62305-2.

In any case, the Supplier of the odourisation plant is responsible for making the earthing connections of all the masses, extraneous masses of the conductive parts up to the equipotential earth point (node), also for the purpose of protection against indirect contacts (see CEI 64-8) and electrostatic charges, in addition to the supply and installation of any overvoltage protectors (SPD) on the odourisation plant electricity supply circuits, which may be deemed necessary.

Any electrical/electronic equipment relating to the odourisation plant must be designed, constructed and installed "to standard", so as to create a plant that is suitable for locations with a risk of explosion due to the presence of gas, in accordance with the provisions of standards CEI 64-8 and CEI EN 60079-14.

Particular reference must be made to the latter standard for the choice of types of electrical constructions, the criteria for their installation and the relevant ducts; this is in relation to the site qualification, defined in the plant classification document, in accordance with the provisions of Legislative Decree no. 81/08, as amended, Title XI.

## Containment system

Newly built odourisation plants must be fitted in correspondence with all parts, such as service tanks (fixed or mobile), dosing system, decanting system etc., with suitable structures or accessories to contain any odorant that may have leaked in accordance with the provisions of Standard UNI 9463-2. The construction of new odourisation plants, or the retrofitting of existing ones, must include verification that the containment structure (new or existing) is suitable/compliant in order to prevent infiltration and dispersion into the ground of any odorant leakages. In the case of unsuitability/non-conformity of the existing structures, appropriate retrofitting must be provided.

Below, by way of example, the descriptions of the containment systems provided for in Section 4.5.4 of Standard UNI 9463-2, graphically represented in Annexes 4 and 5 to this specification, are provided:

- Annex 4: The containment system must convey the accidentally spilt odorant by gravity to a collection tank with a capacity of > 1500 but < 1700 m3. It must be equipped with means of neutralising the spilt odorant, with sufficient capacity for the amount of liquid odorant remaining after it has been conveyed into the collection tank. The containment-tank connection must be made with pipe that can be shut-off by a manual valve with a diameter > 1", equal to the pipe used. The collection tank must be equipped with a vent pipe shut-off valve (both 1" in diameter), and an odorant recovery valve, also 1" in diameter. The vent pipe (protected against accidental entry of foreign bodies and/or rainwater) must be connected to a vapour abatement or absorption system.

- Annex 5: The containment system must convey the accidentally spilt odorant by gravity to a collection tank with a capacity of > 2700 but < 3000 m3. It must be equipped with means of neutralising the spilt odorant, with sufficient capacity for the amount of liquid odorant remaining after it has been conveyed into the collection tank. The containment-tank connection must be made with pipe that can be shut-off by a manual valve with a diameter > 1", equal to the pipe used. The collection tank must be equipped with a vent pipe shut-off valve (both 1" in diameter), and an odorant recovery valve, also 1" in diameter. The vent pipe (protected against accidental entry of foreign bodies and/or rainwater) must be connected to a vapour abatement or absorption system.

## Technical assessment

In relation to Legislative Decree no. 81/08 as amended and supplemented, Italgas Reti reserves the right, in its evaluation of the use of the proposed products, to consider the operational consequences deriving from the conditions of use of the equipment as prescribed by the Supplier in the "Use and Maintenance Manual".

# DOCUMENTATION REQUIRED FROM THE SUPPLIER

## Supplier()

- The potential Supplier must be qualified as an ITALGAS RETI Supplier and must be able to provide after sales services directly in Italy.

## Documentation for the company approval process

The potential Supplier must submit the following documentation to the PROMA-CMMAT Department:

“Declaration of Conformity” with this technical specification and any specific documents (legislative provisions, applied standards, etc.) to which the supplier refers for the design and construction of the product, in accordance with the requirements of UNI CEI EN ISO/IEC 17050-1 (see the example in appendix 4 to this technical specification).

## Marking and labelling

Each drum/tank must be marked with the information stipulated in Section 4.9.3 of UNI 9463-2.

## Test Documentation

The Supplier must issue a “type 3.1” Inspection and Material Certificate in accordance with UNI EN 10204, stating that the products provided are compliant with the requirements of these specifications as well as the legislative provisions as per point 7.

The Supplier must also produce a test report for each test containing at least the following information:

- Name of the authorised person responsible for the test;

- Test date;

- Manufacturer of the plant;

- Client or interested party;

- Identification of the section to which the test relates;

- Design pressure;

- Pressure reached during the test and the time for which it was maintained;

- Test fluid;

- Test result;

- Reference to the test procedure;

- Instrumentation used for the test with indication of calibration validity;

- Type and serial number of the instrument used for the test.

Registration of the full production/test documentation completed by the Supplier must be kept on the basis of legal provisions for 10 years under its responsibility, and must be made available whenever requested by the Client.

## Documentation accompanying the supply

Each odourisation plant must be delivered accompanied by a technical file (Data-Book) containing at least the following documentation:

  - "EU Declaration of Conformity" in accordance with recent legislative decrees implementing the Directives applicable to the product (e.g. ATEX, PED Directives etc.);

  - ATEX exclusion declaration for tanks and drums;

  - Copy of the "Installation, Use and Maintenance Manual" (in Italian) for the correct use of the product;

  - Inspection and quality plan;

  - “Type 3.1” Inspection and Material Certificates in accordance with UNI EN 10204;

  - Declaration of conformity and compliance with UNI 9463-2;

  - Declaration of conformity with applicable legislation;

  - Test report;

  - Any other technical documents and/or drawings requested by the relevant Italgas Reti departments;

  - Construction drawings of the plant;

  - Documentation showing the characteristic data of the tanks, necessary for carrying out periodic integrity checks;

  - "Intrinsically safe system description document" (if any);

If the odourisation system is to be supplied on a turnkey basis, the Supplier must issue a declaration of conformity pursuant to Ministerial Decree no. 37 of 22 January 2008, as amended.

# TESTS AND INSPECTIONS

## Type tests

During the design phase of the product, it shall be the Supplier's responsibility to carry out at recognised laboratories or directly at the Supplier's premises all the "Type Tests" required by the reference standards and/or the Supplier's own design standards and the standards referred to therein, to verify the intended end use of the product.

## Tests and inspections

The tests and inspections described below must be carried out by the Supplier on each plant supplied:

- Visual and dimensional inspection (point 6.3);

- Mechanical strength test (point 6.4);

- Leak test (point 6.5);

- Non-destructive testing of welds (point 6.6).

## Visual and dimensional inspection

The construction and dimensional conformity with the construction drawing must be checked.

The dimensional tolerances of the threads must be those specified in the relevant standards.

The inspections must be certified in accordance with UNI EN 10204 type 3.1.

## Mechanical strength test

### Main gas circuit

Before the installation is assembled, all the pressure components of the main gas circuit, including the pipes constituting the plant, must undergo a mechanical strength test at the factory, which must be recorded. Test procedures must be chosen according to UNI EN 12327.

The mechanical strength test must have a minimum duration of 4 hours, after temperature stabilisation, and must be performed under the conditions specified below in Table 2:

Table 1: Mechanical strength test pressures

| Test pressure Pcol | MOP |
| --- | --- |
| 2.5 bar | for system sections with MOP ≤ 1.5 bar |
| 7.5 bar | system sections with 1.5 bar < MOP ≤ 5 bar |
| 18 bar | for system sections with 5 bar < MOP ≤ 12 bar |

For pipelines with a diameter not exceeding 100 mm and for those with MOP ≤ 5 bar, the test can be performed using natural gas, air or inert gas; for all other conditions, the test must be performed hydraulically.

For pipelines with a diameter of more than 100 mm, the air or gas test may be carried out in cases of recognised difficulty in carrying out the hydraulic test, for sections of pipeline or plant of limited volume, provided that all necessary measures are taken to carry out the tests under safe conditions.

Pressure equipment for which a factory test is to be carried out in accordance with the relevant regulations may be excluded from the mechanical strength test.

If the Supplier can prove by means of suitable existing documentation that the components of the main gas circuit have been previously tested at least to the required test pressure (see Table 2), the strength test need not be repeated on these components.

### Dosing drum and Service tank

Each dosing drum and each service tank supplied must be hydraulically tested in accordance with Section 7.4 of Annex I of Legislative Decree no. 93/00, as amended. The duration of the test must be at least 30 min.

## Leak test

After the strength test has been passed, all the components that were removed from the main gas circuit before the test must be reinstalled.

The entire installation must be subjected to a pneumatic leak test.

The test must have a minimum duration of 30 minutes, after temperature stabilisation, and must be carried out at maximum operating pressure.

Air or inert gas or mains gas can be used as test fluid.

At the end of the  leak test, a "Test Report" must be drawn up in accordance with Section 4.10.5 of UNI 9463-2.

## Non-Destructive Testing (NDT) of welds

Welding of steel pipes must be carried out in accordance with UNI EN 12732, according to qualified procedures complying with UNI EN ISO 15614-1 or equivalent standards.

Welders must be qualified in compliance with UNI EN ISO 9606-1 or equivalent standards.

All non-destructive testing operations indicated below must be carried out by qualified Level 2 personnel in accordance with formalised procedures. Level 2 personnel must be certified in compliance with UNI EN ISO 9712.

The non-destructive testing (NDT) to be carried out on welded joints subjected to pressure must include at least the following checks:

- Main gas circuit:

Head-to-head welds must be radiographed at 20% in accordance with Italgas Reti and in compliance with UNI EN 17636-1 (Class B); the acceptability level is level 1 according to UNI EN 10675-1.

- Service tank and dosing drum:

All head-to-head welds, whether circumferential or longitudinal, must be radiographed at 100% in compliance with UNI EN ISO 17636-1 (Class B); the acceptability level is level 1 according to UNI EN ISO 10675-1.

Any welds that cannot be radiographed must be checked 100% with liquid penetrants in accordance with UNI EN ISO 3452-1, acceptability level 1 to UNI EN ISO 23277 or with magnetic particles in accordance with UNI EN ISO 17638, acceptability level 1 according to UNI EN ISO 23278.

## Right of the Client

In order to verify the conformity of the proposed products with the contents of this technical specification and the cited standards to which reference is made, it is Italgas Reti's right to request from the Supplier:

  - The production of relevant technical and/or graphic documentation with the indicated characteristics;

  - The performance of any laboratory and/or field tests in relation to the required product characteristics.

# REFERENCE STANDARDS

- Law no. 186 of 1 March 1968 "Provisions concerning the production of materials, equipment, machinery, electrical and electronic installations and systems".

- Legislative Decree No. 85 of 19 May 2016 - “Implementation of Directive 2014/34/EU on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres”.

- Legislative Decree No. 233 of 12 June 2003 “Implementation of Directive 1999/92/EC on minimum requirements for improving the safety and health protection of workers exposed to the risk of explosive atmospheres”.

- Italian Legislative Decree no. 81 of 9 April 2008, as amended  “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”.

- Italian Legislative Decree no. 206 of 06 September 2005, as amended – “Consumer code pursuant to Article 7 of Law no. 229 of 29 July 2003”.

- Italian Legislative Decree no. 194 of 6 February 2007, as amended (Legislative Decree no. 80 of 18 May 2016) "Implementation of Directive 2004/108/EC on electromagnetic compatibility, and Directive 2014/30/EU of 26 February 2014 on the harmonisation of the laws of the Member States relating to electromagnetic compatibility (recast) providing for its repeal".

- Legislative Decree No. 93 of 25 February 2000, as amended 'Implementation of Directive 97/23/EC on pressure equipment and Directive 2014/68/EU on the harmonisation of the laws of the Member States relating to the making available on the market of pressure equipment (recast), providing for its repeal'.

- Ministerial Decree of 16 April 2008 “Technical regulations for the design, construction, testing, operation and supervision of works and distribution systems and direct lines for natural gas with a density not exceeding 0.8”;

- Ministerial Decree no. 37 of 22 January 2008, as amended “Regulation on the implementation of Article 11-quaterdecies, subsection 13, letter a) of Law no. 248 of 2 December 2005, on the reorganisation of the provisions on the installation of systems inside buildings”.

- UNI 9463-1 "Odourisation plants and odorant storage for combustible gases for domestic or similar use – Part 1: Terms and Definitions".

- UNI 9463-2 "Odourisation plants and odorant storage for combustible gases for domestic or similar use – Part 2: Odourisation plants - Design, construction, testing and surveillance".

- UNI 7133 "Gas odourisation for domestic and similar uses".

- UNI 9734 “Shut-off devices for gas pipelines. Steel valves with ball obturator”.

- UNI CEI EN ISO/IEC 17050-1 - "Conformity assessment - Supplier's declaration of conformity - Part 1: General requirements".

- UNI EN 10028 "Flat products made of steel for pressure vessels”.

- UNI EN 10028-7 "Flat products made of steel for pressure vessels - Part 7: Stainless steels"

- UNI EN 10204 “Metallic products - Types of inspection documents”.

- UNI EN 12327 "Gas infrastructures - Pressure testing, commissioning and decommissioning procedures for gas supply networks - Functional requirements".

- UNI EN 12732 "Gas infrastructures - Welding of steel pipework - Functional requirements".

- UNI EN ISO 15614-1 “Specification and qualification of welding procedures for metallic materials - Welding procedure test - Part 1: Arc and gas welding of steels and arc welding of nickel and nickel alloys”.

- UNI EN ISO 9606-1 “Qualification testing of welders - Fusion welding - Part 1: Steels”.

- UNI EN ISO 9712 "Non-destructive testing - Qualification and certification of non-destructive testing personnel".

- UNI EN ISO 17636-1 "Non-destructive testing of welds - Radiographic testing - Part 1: X and gamma-ray techniques with film".

- UNI EN ISO 17638 "Non-destructive testing of welds - Magnetic particle testing".

- UNI EN ISO 10675-1 "Non-destructive testing of welds - Acceptance levels for radiographic inspection - Part 1: Steel, nickel, titanium and their alloys".

- UNI EN ISO 3452-1 “Non-destructive testing - Penetrant testing - Part 1: General Principles”.

- UNI EN ISO 23277 "Non-destructive testing of welds - Penetrant testing - Acceptance levels".

- UNI EN ISO 23278 "Non-destructive testing of welds - Magnetic particle testing - Acceptance levels".

- CEI 64-8 "Electrical consumer systems at normal voltage not exceeding 1,000 V alternating current and 1,500 V direct current".

- CEI EN 60079-14 (CEI 31-33) - "Electrical apparatus for explosive gas atmospheres. Part 14: Electrical Installations in places with danger of explosion due to the presence of gas (other than mines)"

- CEI EN 62305-1÷4 (CEI 81-10/1÷4) "Lightning protection".

# APPENDICES

## APPENDIX 1 – "Standard connection plate for odorant refilling"

## APPENDIX 2 – "Connection system for bulk odorant refilling from tanker truck"

## APPENDIX 3 – "Magnetic and magnetostrictive indicator of odorant levels"

## APPENDIX 4 – “Sample declaration of conformity with this technical specification”

## APPENDIX 5 – "ATEX Exclusion Declaration (for tanks and drums)".

# annexes

The annexes to this Technical Specification form an integral part thereof. They are issued exclusively by Italgas Reti and selected as the occasion arises according to company needs.

## Annex 1: "Functional diagram of injection odourisation plant and back-up lapping by-pass”.

## Annex 2: "Functional diagram of injection odourisation plant and back-up lapping by-pass with service tank”.

## Annex 3: "Functional diagram of injection odourisation plant and injection back-up plant and 2nd lapping by-pass back-up system".

## Annex 4: "Schematic diagram of pre-assembled apparatus with service tank, spill containment system and collection tank".

## Annex 5: "Schematic diagram of pre-assembled apparatus with two service tanks, spill containment system and collection tank".

## Annex 6: S.T.V.F.C. 9992322 "Filter systems for odourisation plants".

# Appendix 1

STANDARD CONNECTION PLATE FOR ODORANT REFILLING (INSTALLATION REQUIRED AT ALL WRMPs OF ITG RETI)

Description: External galvanised steel plate (dimensions 50 x 50 cm), suitably fixed to the wall where the connections for odorant refilling of the odorant tanks are located, on the outside of the room/cabinet. The aforementioned plate must be connected to the WRMP earthing system by means of PVC-insulated copper or rubber G7 yellow-green cable with a minimum cross-section of  16 mm2.

Examples of construction (non-exhaustive).

Figure 1: Example of an odorant refilling plate to be used for new constructions or replacements.

Note: Today, for the gas phase, Stäubli type RBE06 couplers are installed on many WRMPs (instead of the SBA08 coupler); it is the responsibility of the odorant Supplier to have a suitable adapter available.

Figure 2: Example of an odorant refilling plate commonly found on ITGR's WRMPs today.

These are kept in use until they need to be replaced (see Figure 1).

# Appendix 2

CONNECTION SYSTEM FOR BULK ODORANT REFILLING FROM TANKER TRUCKS (ONLY FOR SPECIALLY PREPARED WRMPs)

Description: 2” coupler for tank connection, wall-mounted near the outer plate (Appendix 1), positioned with the coupler side down for better cleaning, type DRY-BREAK ™ by Emco Wheaton, suitable for transferring liquids without spillage.

How it works: After connecting to the tank unit by turning the tube unit 15 degrees clockwise, the half couplers lock together.

At this point the valves are still closed and will not open until a further 90 degree rotation is performed.

The product can now flow. To close the valve and unlock the units, reverse the procedure.

# Appendix 3

MAGNETIC ODORANT LEVEL INDICATOR

Description	Magnetically operated odorant level indicator (Colima type) installed on each individual drum and service tank(s).

Side mounting outside the tank

Flange or thread side/side connections

Specifically for pressure tanks containing methane gas.

MAGNETOSTRICTIVE ODORANT LEVEL INDICATOR

Description	ATEX-compliant level sensor device of the magnetostrictive type with 4-20 mA signal transducer complete with correction for litres of odorant remaining in the drum/tank, with analogue signal output for connection to the remote control system of the WRMP plant.

Mounted on the side outside the tank or directly in the tank

Flange or thread side/side connections

Specifically for pressure tanks containing methane gas.

Examples of construction (non-exhaustive).

# Appendix 4

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN lSO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: .............................................................................................................................................................................

Address of the issuer: .............................................................................................................................................................................

(3)	Subject of the declaration: .............................................................................................................................................................................

.............................................................................................................................................................................

.............................................................................................................................................................................

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(4)	T.S. 9992320	Odourisation plants	Edition 5 of 25.09.2019

Additional information:

(5) .........................................................................................................................................................................

...............................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(6) 	............................................................. 		         .................................................................................

(Name and position)				(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- List all the products for which approval for company use is requested (name, type, model), stating any codes assigned by the Supplier itself and, where existing, the relevant material codes assigned by Italgas Reti.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

# Appendix 5

ATEX Exclusion Declaration

We ..............................................................................................................................................................

(name of organisation)

with registered office in .............................................................................................................

(address)

as the .................................................................................................................................................

(Manufacturer / Authorised Representative)

declare under our sole responsibility that the products series

.....................................................................................................................................................................

.....................................................................................................................................................................

(name, type or model, batch, group or serial numbers)

described in the Technical Specification / document(s)

.....................................................................................................................................................................

.....................................................................................................................................................................

(when necessary)

to which this declaration refers, comply with the following legislative / regulatory document(s)

.....................................................................................................................................................................

.....................................................................................................................................................................

(title(s) and/or number(s) and date(s) of publication of the standard(s) or other legislative and/or regulatory document(s))

and, according to Article 1, subsection 1a) of Directive 2014/34/EU of 26 February 2014 (Legislative Decree no. 85 of 19 May 2016) and Chapter 1 of ATEX 2014/34/EU GUIDELINES (first edition), based on an ATEX analysis (see subsection 32 of the aforementioned ATEX 2014/34/EU GUIDELINES), do not fall within the scope of the Directive 2014/34/EU, as they do not risk causing an explosion due to the lack of potential ignition sources, as defined in Standard UNI EN 1127-1, when used in systems that comply with the following legislative and/or regulatory documents

.....................................................................................................................................................................

.....................................................................................................................................................................

.....................................................................................................................................................................

(title and/or number and date of publication of legislative and/or regulatory documents)

They can therefore be installed in all types of zones as defined in Legislative Decree no. 81 of 9 April 2008, as amended, Title XI (Directive 1999/92/EC of 16 December 1999).

..................................................................                    ......................................................................................

(place and date of issue)		(name and signature or equivalent stamp of authorised person)

See Law no. 186 of 1 March 1968 and Legislative Decree no. 81 of 9 April 2008, Article 81

Supplier means the party responsible for the design and construction of the products or its legal representative as defined in Legislative Decree no. 206 of 6 September 2005 as amended and supplemented. - "CONSUMER CODE" pursuant to Article 7 of Law no. 229 of 29 July 2003.