“TECHNICAL SPECIFICATION”

S.T. 9992324

SOLENOID VALVE WITH INTEGRATED SENSOR FOR ODOURISATION PLANTS

| Compiled by | SERTEC-CORID | CAMPISANO, RAFFAELLO |
| --- | --- | --- |
|  | SERTEC-NORM | IRRERA, ANDREA |
| Checked by | SERTEC-CORID | FERRACUTI, GIOVANNI |
|  | SERTEC-NORM | VARESE, ENRICO |
|  | SERTEC-LAB | SALATI, EUGENIO |
|  | PROMA-MATMA | SCOTTO, ENRICO |
|  | PROMA/CMMAT | FASSINO, SILVIO |
|  | HSEQ | LIMONTA, AGOSTINO MASSIMO |
| Approved by | SERTEC | PISINO, FEDELE |

SUMMARY

1	PRELIMINARY INFORMATION	3

1.1	Cancels and replaces	3

1.2	Reason for issue	3

1.3	Definitions	3

2	PURPOSE AND FIELD OF APPLICATION	3

2.1	Purpose	3

2.2	Field of application	3

3	SPECIFICATIONS	3

4	TECHNICAL CHARACTERISTICS	4

4.1	Operating principle	4

4.2	Construction characteristics	4

4.3	Technical assessment	5

5	DOCUMENTATION REQUIRED FROM THE SUPPLIER	5

5.1	Supplier	5

5.2	Documents to be submitted	5

5.3	Marking and labelling	5

5.4	Test Documentation	6

5.5	Documentation accompanying the supply	6

6	TYPE TESTS	6

6.1	Right of the Client	6

7	REFERENCE STANDARDS	6

8	annexes	7

9	APPENDICES	7

Appendix 1	8

# PRELIMINARY INFORMATION

## Cancels and replaces

This technical specification cancels and replaces:

- T.S. 9992324, Edition 1, dated 07/09/2020 "Solenoid valve with integrated sensor for odourisation plants".

## Reason for issue

The update of T.S. 9992324, Edition 1, dated 07/09/2020 became necessary in order to eliminate a typo in the text, concerning the classification of the solenoid valve in relation to the type of operation and to extend the range of permissible nominal diameters.

## Definitions

For definitions of the technical terms used in this specification, please refer to the relevant regulations, a non-exhaustive list of which can be found in point 7. Unless explicitly referred to otherwise, the standards cited are those in the latest edition, including any variants/updates and/or corrigenda published.

# PURPOSE AND FIELD OF APPLICATION

## Purpose

To define the technical product characteristics, the technical testing procedures to be followed and the criteria for the supply and testing for approval for company use of solenoid valves with integrated sensor to be used in the odourisation plants as per T.S. 9992320 (Annexes  1, 2 and 3, pos. no. 30).

## Field of application

This specification applies, in the case of direct purchase by Italgas Reti, whenever the opportunity arises to procure a material subject to this T.S. produced by a new potential Supplier or by an existing Supplier; it is also applied to define the characteristics of the products in question when they are supplied by an installer.

# SPECIFICATIONS

These technical specifications must be understood as an integral part of the “ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS”.

This specification contains the minimum technical requirements demanded by Italgas Reti based on the reference legislative and technical standards.

It is the Supplier's responsibility to ensure that the products supplied fully comply with the provisions of this technical specification and current legislation.

If the materials in question are supplied by an installer, the installer must document their compliance.

It is also the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. sharp edges or incorrect directions for use and maintenance), which may jeopardise the health and safety of the Client's workers in relation to the provisions of Italian Legislative Decree no. 81/08, as amended and supplemented.

For any technical and operational aspects that conflict with or are not mentioned in this Technical Specification but that nevertheless pertain to the design, installation, maintenance and use of the products, it is the Supplier's responsibility to refer to the legislation and regulations in force.

# TECHNICAL CHARACTERISTICS

## Operating principle

The solenoid valve with integrated sensor covered by this Specification is of the normally open (N.O.) type and, under normal operating conditions of the odourisation injection plant is positioned in the closed position, preventing the transit of natural gas to the part of the lapping odourisation system bypass.

In the event of a malfunction of the injection odourisation plant, an "odourisation plant alarm" (OPA) is generated by the remote control system; the resulting signal interrupts the voltage on the solenoid valve coil, causing it to open and thus allowing the gas to be odourised to flow into the odourisation system bypass (lapping). Simultaneously with the opening of the bypass solenoid valve, the latter, being equipped with a special on/off sensor, generates a "lapping in operation" (LIO) signal.

When the anomaly and the OPA cease, the solenoid valve switches back to the closed position, thus returning the gas odourisation system to its normal operating set-up (primary injection odourisation system and back-up system with gas bypass). The return to standard operation is reported to the Integrated Supervision Centre (ISC).

## Construction characteristics

Two-way, normally open, mixed-action solenoid valve suitable for obstructing fluids (including natural gas) compatible with construction materials, with light-alloy coil housing.

Equipped with a built-in proximity sensor with inductive REED technology for monitoring the status of the solenoid valve.

Suitability for installation in places with danger of explosion due to the presence of gas, classified as "zone 1" according to CEI EN 60079-10-1 (CEI 31-87) for the complete product (solenoid valve + sensor), proven by certification according to Legislative Decree 85/2016 (Directive 2014/34/EU - ATEX) at least for category 2G IIA T3 (e.g. protection mode "d" according to CEI EN 60079-1 for the solenoid valve and protection mode "m" according to CEI EN 60079-18 for the sensor). The aforementioned product installation must be carried out in compliance with CEI EN 60079-14 (CEI 31-33).

The main characteristics are summarized below:

- SOLENOID VALVE

- maximum allowed pressure (AP): 24 bar;

- nominal voltage: 12 V DC / 24 V DC / 230 V AC;

- degree of protection: at least IP 67 according to CEI EN 60529 (IEC 70-1);

- fitting type: G ¾" – 1" – 1 ½" – 2" according to UNI EN ISO 228/1;

- seals in fluorinated elastomer (Viton);

- equipped with a terminal for earthing connection.

- PROXIMITY SENSOR

- power supply at a maximum voltage of 30 V DC;

- degree of protection: at least IP 67 according to CEI EN 60529 (IEC 70-1);

- with LED integrated in the sensor for display of operating status on the valve also;

- complete with overload, short-circuit and reverse polarity protection;

- complete with multi-core cable, cross-section 3 x 0.35 mm2 for connection, with characteristics appropriate to the installation environment, at least 2 m long.

## Technical assessment

In relation to Legislative Decree 81/08, as amended and supplemented, Italgas Reti reserves the right, in its evaluation of the use of the proposed products, to consider the operational consequences deriving from the conditions of use of the equipment as prescribed by the Supplier in the "Use and Maintenance Manual".

# DOCUMENTATION REQUIRED FROM THE SUPPLIER

## Supplier

- The potential Supplier must be qualified as an ITALGAS Supplier.

## Documents to be submitted

The potential Supplier must submit to the PROMA/CMMAT Department the “Declaration of Conformity” with this technical specification and any specific documents (legislative provisions, applied standards, etc.) to which the supplier refers for the design and construction of the product, in accordance with the requirements of UNI CEI EN ISO/IEC 17050-1 (see the example in appendix 1 to this technical specification).

## Marking and labelling

The products covered by this T.S. must be provided with the markings required by the EU Directives and by the relevant applicable technical standards, considering that the affixing of the CE marking, together with any other markings (mandatory and/or optional) that may be used, is subject to the provisions of Decision no. 768/2008/EC of 9 July 2008 on a common framework for the marketing of products, implemented by the legislative decrees transposing the applicable product Directives, a non-exhaustive list of which is given under "Legal references" in this T.S.

They must therefore bear the conformity marking , affixed in the manner provided for by the legal provisions in force, together with any other markings provided for by the same directives in relation to the specific execution and configuration (e.g. "specific marking of explosion protection"  - ATEX, marking relating to the disposal of electrical and electronic equipment  - WEEE, etc.).

## Test Documentation

The Supplier must issue a “type 3.1” inspection certificate in accordance with UNI EN 10204, which states that the products provided are compliant with the requirements of this specifications, as well as the regulatory provisions as in point 7, in which the test results are provided.

Registration of the full production/test documentation completed by the Supplier must be kept on the basis of legal provisions, for ten years under its responsibility, and must be made available whenever requested by the Client.

## Documentation accompanying the supply

Each supply of materials covered by these technical specifications (S.T.) must be accompanied by all documentation envisaged by the applicable legislative and regulatory provisions and, in particular, the following documents:

- documents compliant with Legislative Decree no. 286 of 21 November 2005, as amended.

- EU declaration of conformity, written in Italian, as per the implementing Decrees of the applicable product directives (e.g. ATEX, PED, EMC, RoHS, etc.);

- manual for installation, use and maintenance, written in Italian.

# TYPE TESTS

In the design phase of the product, the "Type Tests" required by the Reference Standards and/or the Supplier's design standards and by the standards referred to therein, for verifying the intended end use of the product must have been performed.

## Right of the Client

In order to verify the conformity of the proposed products with the contents of this technical specification and the cited standards to which reference is made, it is Italgas Reti's right to request from the Supplier:

  - the production of relevant technical and/or graphic documentation with the indicated characteristics;

  - the performance of any laboratory and/or field tests in relation to the required product characteristics.

# REFERENCE STANDARDS

- Law no. 186 of 1 March 1968 "Provisions concerning the production of materials, equipment, machinery, electrical and electronic installations and systems".

- Legislative Decree No. 85 of 19 May 2016 - “Implementation of Directive 2014/34/EU on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres”.

- Italian Legislative Decree no. 81 of 9 April 2008, as amended  “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”.

- Italian Legislative Decree no. 194 of 6 February 2007, as amended (Italian Legislative Decree no. 80 of 18 May 2016) "Implementation of Directive 2004/108/EC on electromagnetic compatibility, and Directive 2014/30/EU of 26 February 2014 on the harmonisation of the laws of the Member States relating to electromagnetic compatibility (recast) providing for its repeal".

- Italian Legislative Decree no. 93 of 25 February 2000, as amended 'Implementation of Directive 97/23/EC on pressure equipment and Directive 2014/68/EU on the harmonisation of the laws of the Member States relating to the making available on the market of pressure equipment (recast), providing for its repeal'.

- Ministerial Decree of 16 April 2008 “Technical regulations for the design, construction, testing, operation and supervision of works and distribution systems and direct lines for natural gas with a density not exceeding 0.8”.

- CEI EN 60079-0 (CEI 31-70) - “Explosive atmospheres - Part 0: Equipment - General Requirements".

- CEI EN 60079-1 (CEI 31-58) “Explosive atmospheres - Part 1: Equipment protected by explosion-proof enclosures "d".

- CEI EN 60079-10-1 (CEI 31-87) “Explosive atmospheres - Part 10-1: Classification of areas - Explosive gas atmospheres".

- CEI EN 60079-14 (CEI 31-33) “Explosive atmospheres - Part 14: Design, selection and installation of electrical systems".

- CEI EN 60079-18 (CEI 31-77) “Explosive atmospheres - Part 18: Equipment with protection by encapsulation "m".

- UNI 9463-1 "Odourisation plants and odorant storage for combustible gases for domestic or similar use – Part 1: Terms and Definitions".

- UNI 9463-2 "Odourisation plants and odorant storage for combustible gases for domestic or similar use – Part 2: Odourisation plants - Design, construction, testing and surveillance".

- UNI CEI EN ISO/IEC 17050-1 - "Conformity assessment - Supplier's declaration of conformity - Part 1: General requirements".

- UNI EN 10204 “Metallic products - Types of inspection documents”.

# annexes

The annexes to this Technical Specification form an integral part thereof.

- Annex 1: “S.T.V. 9992320 – Odourisation plants".

# APPENDICES

- APPENDIX 1 – “Sample declaration of conformity with this technical specification”.

# Appendix 1

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN lSO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(4)	TS 9992324	Solenoid valve with integrated sensor for odourisation plants	Edition 2 of 16/10/2020

Additional information:

NOTE:

SAMPLE

(5) 	...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(6) 	....................................................... 			      ..................................................................................................................

(Name and position) 					(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- List all the products for which approval for company use is requested (name, type, model), stating any codes assigned by the Supplier itself and, where existing, the relevant material codes assigned by Italgas.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

Supplier means the party responsible for the design and construction of the products or its legal representative.