“TECHNICAL SPECIFICATION FOR EVALUATION, SUPPLY AND TESTING”

T.S. 2327300

Final reduction unit from road pipes with upstream pressure between 0.5 and 5 bar

| Compiled by | SERTEC-NORM | LORO, SILVIO |
| --- | --- | --- |
| Checked by | SERTEC-NORM | VARESE, ENRICO |
| Checked by | PROMA-MATMA | SCOTTO, ENRICO |
| Checked by | PROMA/CMMAT | FASSINO, SILVIO |
| Checked by | SERTEC-LAB | SALATI, EUGENIO |
| Checked by | HSEQ | BOLZONI, GIANLUCA |
| Approved by | SERTEC | COMAZZI, MARCO |

SUMMARY

1	PRELIMINARY INFORMATION	4

1.1	Cancels and replaces	4

1.2	Reason for issue	4

1.3	Company departments mentioned in the document	4

1.4	definitions	4

2	PURPOSE AND FIELD OF APPLICATION	7

2.1	Purpose	7

2.2	Field of application	7

3	Specifications	7

4	Technical characteristics	8

4.1	Sizing criteria	8

4.1.1	General considerations	8

4.1.2	Design pressure	9

4.1.3	Diameters	9

4.2	Standard plants	9

4.3	Meshed network reduction units	11

4.4	Reduction unit for antenna networks	13

4.5	Technical assessment	15

5	CONSTITUENT ELEMENTS	15

5.1	Circuit breakers	15

5.1.1	Electric circuit breakers	15

5.1.2	PE/steel transition joints	15

5.2	Reduction line	15

5.2.1	Upstream shut-off device	16

5.2.2	Filter	16

5.2.3	Blocking valve	17

5.2.4	Pressure reducer-regulators	17

5.2.5	Device for discharge into the atmosphere	19

5.2.6	Downstream shut-off device	20

5.3	By-pass line (manual)	20

5.4	Emergency line	20

5.5	Control devices and accessories	20

5.6	Electrostatic discharge protection	22

5.7	Pipes, joints and special parts	23

5.7.1	Materials	23

5.7.2	Joints	23

5.8	Protective coating (painting)	23

6	Marking	24

7	MACHINING TOLERANCES	24

8	HOUSING	25

9	ABATEMENT OF ACOUSTIC EMISSIONS	26

10	TYPE TEST	27

11	DOCUMENTATION required from the supplier	27

11.1	Supplier	27

11.2	Documentation for the company approval process	27

11.3	Test Documentation	27

11.4	Supply Documentation	28

12	Tests and inspections	29

12.1	Visual and dimensional inspection	30

12.2	Mechanical strength test	30

12.3	Pneumatic external leak test	30

12.4	Functional tests	31

12.4.1	Check calibration of the regulation pressure of the pressure reducer-regulator with service function	31

12.4.2	Check regulation pressure with zero flow	31

12.4.3	Check regulation pressure and triggering of pressure reducer-regulator with emergency function (monitor)	31

12.4.4	Check triggering of the relief device	31

12.4.5	Check calibration of the maximum regulation pressure blocking valve	31

12.5	Non-Destructive Testing (NDT) of welds	31

12.6	Right of the client	32

13	Conditions of Supply	32

13.1	Packaging	32

14	REFERENCE STANDARDS	32

15	ATTACHMENTS	35

16	Appendices	35

Appendix 1	36

Appendix 2	36

Appendix 3	37

# PRELIMINARY INFORMATION

## Cancels and replaces

This specification cancels and replaces technical specifications 2327300, edition 1, dated 12.11.2012 "Final reduction units from road pipes with upstream pressure between 0.5 and 5 bar”.

## Reason for issue

The update of the Technical Specification 2327300 was required as a result of:

- issuing of new national and European standards (e.g. UNI, CEI, EN, etc.)

- New legislative context;

- updating of Supply and Testing Criteria;

- New company choices.

## Company departments mentioned in the document

- HSEQ = Health, Safety, Environment & Quality;

      - PROMA-CMMAT = Category Manager Materials

      - SERTEC-NORM = Technical Services-Technical Standards

## definitions

Unless otherwise specified the flow rates are in Sm3/h , with gas at 15 °C and 1.013 bar (absolute pressure).

Cabinet:

Containment construction for the control system entirely above ground.

Housing:

A construction for containment of the equipment constituting the pressure control and/or metering plant, of reduced dimensions, inside which there is generally no personnel access.

Main circuit:

The main gas circuit consists of pipes, valves, filters, special parts, regulators, in which the gas flows from the pipeline upstream of the control system to the downstream pipeline.

Reduction unit:

An assembled set of pressure reducers-regulators of the ancillary equipment, special parts and pipes connecting them, having the essential function of decompressing a ducted gas from a variable upstream pressure to a regulated downstream pressure at a fixed value.

Control system (plant):

An assembly consisting of a pressure control system.

The system comprises:

- 	apparatus such as pressure vessels, valves, pressure regulators, safety devices, odourisation system, etc. (equipment able to perform a regulating function);

- 	ancillary elements such as pressure gauges, thermometers, sensors, intake taps, etc. (elements able to record individual data of the regulation functions);

- 	connection pipes for various equipment, dielectric and expansion joints;

- 	housing and/or cabin.

Device for discharge into the atmosphere.

A device which remains in the closed position under normal operating conditions which is able to release gas into the atmosphere following an increase in pressure relative to a pre-set trigger value and able to stop the release when the pressure returns below the pre-set maximum pressure value.

Pressure control system:

Combined system comprising the pressure regulation system, pressure safety system, and possibly also the pressure recording and alarm systems.

Pressure regulation system:

A system that ensures the maintenance of a given pressure, within set limits, downstream of the regulating equipment.

Pressure safety system:

A system that, independently of the pressure regulation system, ensures that the outlet pressure of that system does not exceed the safety limits.

Upstream manifold:

- Assembled set of special parts (bends, tees, etc.) and connecting pipes upstream of the shut-off valves of the reduction line and by-pass (the latter not included).

- Downstream manifold:

Assembled set of special parts (bends, tees, etc.) and connecting pipes downstream of the shut-off valves of the reduction line and by-pass (the latter not included).

Reduction line:

An assembled set of the pressure reducers-regulators, safety devices, auxiliary equipment (pilots, pressure intakes) special parts and connection fittings between the shut-off devices located upstream and downstream of the regulating equipment (the latter included).

Temporary operating pressure (TOPu upstream, TOPd downstream):

Maximum effective pressure at which the system can temporarily operate, under the control of the safety device.

Test pressure (Pcol):

Pressure at which the mechanical strength test of the "main gas circuit" is performed.

Delivery flow rate of the plant:

Maximum flow rate to be ensured by the reduction unit at predetermined supply pressure values.

Nominal flow rate of the plant:

Delivery flow rate from the reduction unit at nominal design pressure (1.5 bar), with the required regulation pressure.

Maximum flow rate (Qmax)

Maximum effective flow rate that the control system must be able to deliver, at maximum upstream supply pressure.

Minimum flow rate (Qmin)

Minimum flow rate that the control system must be able to deliver at minimum supply pressure.

Maximum upstream operating pressure (MOPu):

Maximum upstream pressure at which the plant can be used continuously and under normal operating conditions.

Maximum downstream operating pressure (MOPu):

Maximum downstream pressure at which the plant can be used continuously and under normal operating conditions.

Design pressure (DP):

Pressure value which design calculations are based on. For the application of this specification, the value of 1.5 bar (relative) is used.

Required regulation pressure (OPd):

Regulated pressure which the control system, operating within the required range of inlet pressure variation, must provide downstream with the required accuracy class.

Upstream operating pressure (OPu):

Pressure present in the system under operating conditions. In this specification, this is the pressure value used for the selection of the specific FRU for the maximum flow required by the system (flow that can be delivered by the plant). This value may coincide with but not exceed the minimum operating pressure of the road pipe at or near the point of supply of the plant. The following OPu values are envisaged for the application of this specification: 1.5 bar; 1 bar and 0.5 bar (relative).

Minimum upstream pressure (OPumin):

Lower limit of the plant supply pressure.

For the other technical definitions contained in this specification, please see the standards listed in point 14 “Reference standards”.

# PURPOSE AND FIELD OF APPLICATION

## Purpose

The purpose of this specification is to define:

- the design criteria considered by Italgas Reti for the sizing of FRUs to be installed on its distribution networks;

- flow diagrams and plant components;

- the range of use of standardised FRUs in relation to specific supply conditions (pressure upstream of the FRU);

- the acceptance criteria for approval for company use;

- supply and testing criteria.

## Field of application

This specification applies whenever the opportunity arises:

- to purchase and approve for company use a new FRU designed and manufactured by a potential supplier in accordance with the requirements and indications contained in this specification;

- to assess and approve technical changes made to an existing or already approved FRU.

This specification is also applicable, as far as design criteria and equipment components are concerned, for the retrofitting of existing FRUs. In such cases, the most suitable structure in relation to available space and overall conditions should be evaluated on a case-by-case basis.

# Specifications

- These technical specifications must be understood as an integral part of the “ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS”.

- This specification contains the minimum technical requirements demanded by Italgas Reti based on the reference Legislative and Technical Standards.

- It is the Supplier's responsibility to ensure that the products supplied fully comply with the provisions of this technical specification and the applicable standards.

- If the products in question are supplied by an installer, the installer must document their compliance as required under “Documentation required from the Supplier”.

- It is the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. sharp edges or incorrect directions for use and maintenance), which may jeopardise the health and safety of the Client's workers in relation to the provisions of Italian Legislative Decree no. 81/08, as amended and supplemented.

- For any technical and operational aspects that conflict with or are not mentioned in this technical specification but that nevertheless pertain to the design, installation, maintenance and use of the products themselves, it is the Supplier's responsibility to refer to the regulations in force.

# Technical characteristics

Final reduction units are systems that enable the supply of LP networks. (type 7 pipelines) taking gas (natural gas) from road pipes operated in MPB (type 4 and 5 pipelines) and in MPA (type 6 pipelines).

Depending on the type of network for which FRUs are used, the following categories exist:

- Meshed network units

These consist of an automatically operated reduction line and a manual by-pass line.

- Antenna network units

These consist of two automatically operated reduction lines, called main line and emergency line respectively.

## Sizing criteria

### General considerations

The sizing criteria below are based on the following assumptions:

- the gas and its additives, if any, are non-corrosive;

- the system is subjected to stresses due to gas pressure and the effect of temperature variation;

- the design temperature is between –10°C and +60°C.

- The unit is designed to simultaneously ensure:

  - maintenance of the required regulation pressure at values compatible with the proper functioning of the user equipment.

  - continuity of delivery up to a flow rate equal to 70% of the delivery flow rate, with automatic intervention of the secondary line in the event of a failure of the main line.

Each control system must:

- be designed and constructed with materials suitable to withstand the maximum operating pressure (MOP), in compliance with the Ministerial Decree of 16 April 2008, i.e:

  - 5 bar in the part affected by upstream pressure, not including the shut-off valve downstream of the pressure reducers-regulators;

  - 40 mbar for the part downstream of the reduction line or manual by-pass;

- function correctly, guaranteeing the regulated pressure and flow required in relation to predetermined upstream operating pressure values (OPu) within the range 0.5 ÷ 5 bar (relative);

- be equipped with pressure-reduction equipment, and two safety devices, a pressure reducer-regulator with an emergency function (monitor) and a valve to block delivery in the event of an increase in regulated pressure. The integrated design and assembly of regulation and safety equipment in a single valve body are permitted, in compliance with the relevant standards.

This pressure equipment, together with the filters and shut-off valves provided on the system, must be of the approved, CE-marked type in accordance with the PED Directive (2014/68/EU) and must also comply with the requirements of the ATEX Directives 2014/34/EU and 1999/92/EC.

For the sizing and choice of safety devices, reference must be made, unless otherwise specified, to Ministerial Decree of 16 April 2008 and the UNI 8827 standard.

With regard to the sizing of the individual sections constituting the system, please refer to the following points.

### Design pressure

Except in specific cases, the design pressure value to be referred for the geometric sizing of the plant and choice of pressure reducers-regulators is 1.5 bar.

### Diameters

Main line

The plant must be sized so that under the operating conditions defined in Table 1, maintenance of the regulated pressure is guaranteed at the set value within the required accuracy class.

The gas speed must be kept within 30 m/s for the upstream part of the pressure reducer-regulators and 20 m/s for the downstream part, with a maximum tolerance of +10%.

Note:

In the upstream section of the pressure reducer-regulator with service function, a pressure drop of no more than 150 mbar is permissible with clean filter and at design pressure.

Emergency line (FRU in antenna)

The emergency line is sized with the same criteria as the main line with the exception of the flow rate, which is reduced to 70% of that of the main line.

## Standard plants

Depending on the criteria for sizing the individual components and the range of nominal plant flow rates, six standardised reduction units have been defined.

The use of each unit is foreseen for different flow rates depending on the minimum upstream pressure OPumin of the unit, as shown in the following table:

Table 1:flow rates

| - Plant name | - Nominal flow rate of the plant - (Sm3/h) | - Delivery flow rate of the plant - (Sm3/h) |  |
| --- | --- | --- | --- |
|  | - OPu = 1.5 bar | - OPu = 1 bar | - OPu = 0.5 bar |
| - FRU 1 | - 150 | - 140 | - 100 |
| - FRU 2 | - 250 | - 250 | - 200 |
| - FRU 3 | - 650 | - 550 | - 330 |
| - FRU 4 | - 1500 | - 1300 | - 790 |
| - FRU 5 | - 2500 | - 2100 | - 1300 |
| - FRU 6 | - 4000 | - 3300 | - 2000 |

With reference to Figure 1 and Figure 2 the following are the results of analyses for the various standard plants, in compliance with the rules and requirements set out in point 4 of this specification, which define:

- nominal diameters of the upstream/downstream manifolds;

- general structure of the plant with reference to the constituent elements as in point 5 below. “CONSTITUENT ELEMENTS”.

## Meshed network reduction units

Figure 1: Reduction unit for meshed network supply

| - Pos. | - Description | - Q.TY |
| --- | --- | --- |
| - 1 | - PE/steel transition or insulating joint | - - |
| - 2 | - Upstream manifold | - 1 |
| - 3 | - Upstream line shut-off valve | - 1 |
| - 4 | - Filter | - 1 |
| - 5 | - Blocking valve | - 1 |
| - 6 | - Pressure reducer-regulator with a monitor function | - 1 |
| - 7 | - Pressure reducer-regulator with a service function | - 1 |
| - 8 | - Pressure gauge intake tap | - 5 |
| - 9 | - Downstream shut-off device | - 1 |
| - 10 | - Pressure gauge intake tap with dial gauge | - 2 |
| - 11 | - Upstream by-pass shut-off valve | - 1 |
| - 11a | - Spectacle blind disc | - 1 |
| - 12 | - Manual by-pass | - 1 |
| - 13 | - Manual streamlined flow regulation valve | - 1 |
| - 14 | - Device for discharge into the atmosphere | - 1 |
| - 14.1 | - Atmospheric release device calibration control valve | - 1 |
| - 14.2 | - Atmospheric release device shut-off valve | - 1 |
| - 15 | - Downstream manifold | - 1 |
| - 16 | - PE/steel transition or insulating joint | - - |
| - 17 | - Pressure gauge intake tap with dial gauge indicating minimum pressure | - 1 |
| - 18 | - Pressure gauge intake tap with dial gauge | - 1 |

Table 2: geometric sizing of Standard Meshed FRUs

| - Code - material | - Code - FRU | - Flow rate - Nominal - (Sm3/h) | - UND - (mm) | - DND - (mm) | - By-pass - ND - (mm) | - L - (m) |
| --- | --- | --- | --- | --- | --- | --- |
| - 48002327920 | - FRU 1M | - 150 | - 25 | - 50 | - 25 | - 1.0 |
| - 48002327921 | - FRU 2M | - 250 | - 40 | - 65 | - 25 | - 1.0 |
| - 48002327922 | - FRU 3M | - 650 | - 65 | - 100 | - 25 | - 1.0 |
| - 48002327923 | - FRU 4M | - 1500 | - 100 | - 150 | - 40 | - 1.5 |
| - 48002327924 | - FRU 5M | - 2500 | - 150 | - 200 | - 50 | - 1.5 |
| - 48002327925 | - FRU 6M | - 4000 | - 150 | - 250 | - 65 | - 1.5 |

- UND: Nominal diameter of the upstream manifold

- DND: 	Nominal diameter of the downstream manifold

## Reduction unit for antenna networks

Figure 2: Antenna network supply reduction unit

| - Pos. | - Description | - Q.TY |
| --- | --- | --- |
| - 1 | - PE/steel transition or insulating joint |  |
| - 2 | - Upstream manifold | - 1 |
| - 3a | - Upstream shut-off valve (service line) | - 1 |
| - 3b | - Upstream shut-off valve (emergency line) | - 1 |
| - 4a | - Filter (service line) | - 1 |
| - 4b | - Filter (emergency line) | - 1 |
| - 5a | - Blocking valve (service line) | - 1 |
| - 5b | - Blocking valve (emergency line) | - 1 |
| - 6a | - Pressure reducer-regulator with monitor function (service line) | - 1 |
| - 6b | - Pressure reducer-regulator with monitor function (emergency line) | - 1 |
| - 7a | - Pressure reducer-regulator with service function (service line) | - 1 |
| - 7b | - Pressure reducer-regulator with service function (emergency line) | - 1 |
| - 8 | - Pressure gauge intake tap | - 7 |
| - 9a | - Downstream shut-off valve (service line) | - 1 |
| - 9b | - Downstream shut-off valve (emergency line) | - 1 |
| - 10 | - Pressure gauge intake tap with dial gauge | - 5 |
| - 11 | - Device for discharge into the atmosphere | - 1 |
| - 11.1 | - Atmospheric release device calibration control valve | - 1 |
| - 11.1 | - Atmospheric release device shut-off valve | - 1 |
| - 12 | - Downstream manifold | - 1 |
| - 13 | - PE/steel transition or insulating joint |  |
| - 14 | - Pressure gauge intake tap with dial gauge indicating minimum pressure | - 2 |

Table 3- geometric sizing of Standard Antenna FRUs

| - Code - material | Code FRU | - Flow rate - Nominal - (Sm3/h) | - UND - (mm) | - DND - (mm) | - L - (m) |
| --- | --- | --- | --- | --- | --- |
| - 48002327930 | - FRU 1: | - 150 | - 25 | - 50 | - 1.0 |
| - 48002327931 | - FRU 2: | - 250 | - 40 | - 65 | - 1.0 |
| - 48002327932 | - FRU 3: | - 650 | - 65 | - 100 | - 1.0 |
| - 48002327933 | - FRU 4: | - 1500 | - 100 | - 150 | - 1.5 |
| - 48002327934 | - FRU 5: | - 2500 | - 150 | - 200 | - 1.5 |
| - 48002327935 | - FRU 6: | - 4000 | - 150 | - 250 | - 1.5 |

- UND: Nominal diameter of the upstream manifold

- DND: Nominal diameter of the downstream manifold

## Technical assessment

In relation to Legislative Decree 81/08, as amended and supplemented, Italgas Reti reserves the right, in its evaluation of the use of the proposed products, to consider the operational consequences deriving from the conditions of use of the equipment as prescribed by the Supplier in the "Use and Maintenance Manual".

# CONSTITUENT ELEMENTS

## Circuit breakers

### Electric circuit breakers

These are designed to electrically insulate the FRU from the underground steel pipe, cathodically protected.

Where provided, these consist of single-piece steel insulating joints with smooth ends to be butt-welded in accordance with UNI 10285 and Table M. 17850.. "Steel dielectric joint, NP 16, butt-weld ends".

Note:

Electrical circuit breakers do not constitute part of the supply of the FRUs covered by this specification.

### PE/steel transition joints

These are used to connect the polyethylene road pipes with the upstream and/or downstream manifolds of the reduction units, complying with T.S. 1800300 “Polyethylene fittings and special pieces for methane gas pipelines”. They must be of the weld-on type on both materials and comply in particular with the standards:

- UNI EN 1555-2 for the polyethylene part;

- UNI EN ISO 3183 Grade PSL1 (L210 or qualitatively better) for the steel part.

Note:

Transition joints do not constitute part of the supply of FRUs covered by this Specification.

## Reduction line

This consists of the devices and equipment listed in the following paragraphs.

### Upstream shut-off device

It allows manually operated exclusion of the reduction line, particularly during control and maintenance operations.

It consists of a shut-off valve with the following features:

- butterfly type in accordance with UNI 11354 or ball type in accordance with UNI 9734. The use of grey cast iron as a material is not permitted;

- minimum mechanical strength class: NP 16 / ANSI 150;

- flanged connections;

- direct control with removable lever;

- fast operation by 90° rotation of the obturator with end stops in fully open and fully closed position and indication of position reached.

### Filter

It protects the downstream regulation and safety devices from solid particles that may be present in the gas and prevents transfer of the same from the upstream pipeline to the downstream pipeline.

The filter must be equipped with an easily removable cartridge filter element, arranged so that, during operation and maintenance operations, the dust retained by it is prevented from falling into the FRU pipes.

The filtering capacity must be such as to ensure the correct functioning of the regulation and safety device and in any case such as to ensure that solid particles larger than 50 m are stopped with filter cartridges complying with T.S. 9991300 - "Cartridge filter elements for filters of gas reduction and metering units and plants".

It consists of a device with the following features:

- cylindrical body with horizontal axis;

- material: steel or aluminium alloy;

- minimum mechanical strength class of the filter body: NP 6

- flanged connections: NP16 / ANSI 150;

- maximum pressure drop with clean filter element as indicated in UNI 8827.

The filter must be equipped with:

- differential pressure gauge clogging indicator, in accordance with T.S. 9991308 “Measuring and precision indicating instruments for plant installations”, fitted with graduated scale for direct reading of the pressure drop from upstream to downstream of the filtering element, with storage of maximum Δp indicative of the clogging level reached and fitted with manifold;

- pressure intake on the filter outlet section, equipped with a pin pressure gauge holder tap and dial gauge, in accordance with T.S. 9991308 "Measuring and precision indicating instruments for plant installations", Bourdon spring type, metal case, watertight for assembly in the field, with "gas” threaded connection UNI EN 10226 ND 1/2", dial diameter 100 mm, with adequate full scale to allow easy and accurate reading of OPu, which must be between 25% ÷ 75% of full scale value, and maximum error not greater than 2.5% of full scale value;

- ball vent valve, with conveyable release fitted with blind steel cap, connected by means of a chain.

Particular care must be taken when designing the positioning of the filtration system, so that during periods of inactivity of the emergency line, there is no accumulation of dust such as to clog it, jeopardising the automatic start-up of the line in case of need.

### Blocking valve

This remains in the open position under normal operating conditions and stops the gas flow automatically and completely in the event of an increase in the required regulation pressure above the permissible limit.

It consists of a device with the following features:

- steel or spheroidal cast iron body;

- minimum mechanical strength class: NP 16 / ANSI 150;

- flanged in-line connections;

- manually adjustable automatic intervention device (diaphragm pressure switch with contrast spring and threaded connection for impulse tap connected on LP section downstream of the pressure reducer-regulators, adjustable in the range 20 ÷ 50 mbar).

The blocking valve must meet the following requirements:

- the maximum calibration value of the pressure relief valve must be less than or equal to the maximum pressure that the system can achieve for a short period minus the positive tolerance corresponding to the accuracy class of the safety device;

- compliance with UNI EN 14382 and accuracy class at least AG 10 according to table 3 of UNI 8827-2;

- in the event of being triggered, the blocking valve must remain in the closed position and must only be reopened by manual operation.

The delivery blocking valve can be incorporated into one of the pressure reducer-regulators. In this case, it must be mechanically independent of the pressure reducer-regulator; in particular, it must have its own closing seat and obturator and its own measuring element (a device that is directly sensitive to gas pressure).

### Pressure reducer-regulators

Pressure reducer-regulators must be of the type approved for company use, as per Appendix 1 - T.S. 23273. "List of pressure reducers-regulators approved for company use”.

#### Pressure reducer-regulator with emergency function (monitor)

This intervenes to regulate the outlet pressure of the reduction line in the event of downstream overpressure due to failure of the pressure reducer-regulator with service function. During normal operation, the obturator is in the fully open position.

It consists of a fail-close type device with the following features:

- diaphragm type with spring-loaded contrast and pilot operation;

- steel or spheroidal cast iron body;

- minimum mechanical strength class: NP 16 / ANSI 150;

- flanged connections;

- perfect closure with zero flow;

- manual adjustment, from the outside, of the calibration pressure in the range 15 ÷ 35 mbar;

- pilot powered by a stabiliser unit with filter having suitable characteristics for correct operation and meeting the following requirements:

  - upstream pressure range: 0.3 ÷ 5 bar;

  - pressure stabiliser able to maintain constant operating pressure upstream of the pilots (can be built into the pilots).

The pressure reducer-regulator with emergency function (monitor), will be fitted with a quick release device of the motorisation pressure (accelerator valve), directly conveyed to the atmosphere or downstream pipe.

The monitor can be incorporated into the pressure reducer-regulator with service function. In this case, the two pressure reducer-regulators must be mechanically independent; in particular, they must have their own measuring, loading and choking elements (seat and obturator).

The pressure reducer-regulator with emergency function (monitor) must fulfil the following requirements:

- the calibration value must be chosen so that the temporary operating pressure cannot be exceeded;

- any failure of the pressure reducer-regulator with active service function must not jeopardise the proper functioning of the pressure safety system;

- compliance with UNI EN 334 and accuracy class AC 5 according to table 2 of UNI 8827-2.

#### Pressure reducer-regulator with a service function

This regulates the outlet pressure of a reduction line under normal operating conditions.

This consists of a "piloted" type regulator-reducer device with characteristics identical to those indicated in point  above, without the quick release device, or of a "self-activated" type regulator-reducer device with the following characteristics:

- diaphragm type with spring-loaded contrast;

- steel or spheroidal cast iron body;

- minimum mechanical strength class: NP 16 / ANSI 150;

- flanged connections;

- perfect closure with zero flow;

- manual adjustment, from the outside, of the calibration pressure in the range 15 ÷ 35 mbar.

Important:

Although it is not the standard solution, Italgas Reti may specifically request, with a separate quotation, the installation of piloted service pressure reducers-regulators.

Notes:

The combination of the two pressure reducer-regulators and related accessories must guarantee the following performance requirements for the reduction unit during its operation with an upstream operating pressure (OPu) in the range of 0.5 ÷ 5 bar (depending on the maximum upstream operating pressure MOPu):

- the pressure regulation system must keep the pressure within certain acceptable limits for the downstream system. The calibration value must not be greater than the maximum downstream operating pressure MOPd;

- be compliant with UNI EN 334;

- regulation accuracy class (AC): ± 5% of the regulated pressure calibration value, in the range 10 ÷ 100% of the nominal flow rate of the unit;

- closing accuracy class (SG): + 10% max. of the calibration value of the regulated pressure.

To further clarify the above and for brevity’s sake, a summary of the types of regulation and safety equipment approved on the various standardised systems is given in Table 4 . The devices used must have been previously approved for company use, see the list provided for by T.S. 23273…

Table 4: Type of regulation and safety equipment.

| - Plant name | - Nominal flow rate | - Blocking valve | - Pressure reducer-regulator with a monitor function | - Pressure reducer-regulator with a service function |
| --- | --- | --- | --- | --- |
| - FRU 1 | - 150 | - Yes | - P | - A/P |
| - FRU 2 | - 250 | - Yes | - P | - A/P |
| - FRU 3 | - 650 | - Yes | - P | - A/P |
| - FRU 4 | - 1500 | - Yes | - P | - A/P |
| - FRU 5 | - 2500 | - Yes | - P | - A/P |
| - FRU 6 | - 4000 | - Yes | - P | - A/P |

A : 	pressure reducer-regulator device of the "self-activated" type

P : 	pressure reducer-regulator device of the "piloted" type.

### Device for discharge into the atmosphere

This keeps the regulated pressure below the trigger values of the blocking valve in the event of small leakages due to imperfect closing of the pressure reducer-regulators at zero flow.

It has the following characteristics:

- diaphragm type with contrast spring and internal impulse tap;

- steel or light alloy die-cast body;

- threaded "gas" connections UNI EN 10226;

- pressure release manually calibrated, from the outside, in the range 20 ÷ 40 mbar, in accordance with the requirements of UNI 8827-1;

- perfect seal on closing for return of pressure to less than 95% of release pressure.

Upstream of the atmospheric release device, in order to allow calibration and maintenance operations on the same, a shut-off valve must be installed, sealed in the open position, which complies with the requirements of T.S. 2000300 “Steel valves for gas pipelines”.

A pressure intake must be inserted between the shut-off valve and the atmospheric release device for the calibration of the atmospheric release device, consisting of the same elements as indicated in the following point 5.5 a).

The atmospheric release device must be connected to the pipe conveying the gas to the atmosphere, fitted with a terminal vent to prevent obstruction of the outlet due to the ingress of foreign matter (e.g. water, dirt, insects).

### Downstream shut-off device

This allows manually operated exclusion of the reduction line, particularly during control and maintenance operations.

It consists of a shut-off valve with characteristics corresponding to those listed in point 5.2.1 for the upstream shut-off device.

## By-pass line (manual)

Provided for meshed type FRUs, it is fitted with a shut-off device, the characteristics of which are similar to those of the upstream shut-off valve referred to in point 5.2, and a second shut-off device (streamlined flow type) located downstream of the gas flow, which is suitable for manual regulation operations.

A "figure-8" blind disc must be provided and installed immediately downstream of the upstream (gas direction) shut-off valve of the manual by-pass line. This consists of two discs, one blind and one through, joined in the form of glasses, and with a handle, suitable for mounting between flanges, and with mechanical resistance class ANSI 150 / NP 16.

## Emergency line

Envisaged for antenna-type FRUs, it consists of the same components as the main reduction line. Particular care must be taken when designing the positioning of the filter, so that during periods of inactivity of the line, there is no accumulation of dust such as to clog it, jeopardising the automatic activation of the line in case of need.

## Control devices and accessories

All the control devices must be positioned so as to be easy to read by personnel operating and/or carrying out inspections of the FRUs:

- Inlet pressure intake

Allows the pressure of the gas entering the reduction line(s) to be measured. It is placed upstream of the shut-off valve of the main line (on the upstream manifold), is made of a section of quality steel pipe, normally not smaller than ND ½", with one end edge-welded to the pipe, in a front or side position and not at the rear, and the other end "gas" threaded in accordance with UNI EN 10226.

It is fitted with a pin stopcock, fitted with closing cap preferably connected to it by means of a chain.

- Inlet pressure gauge intake

Allows the pressure of the gas entering the reduction line(s) to be measured. It is positioned upstream of the shut-off valve of the main line (on the upstream manifold), and is made as in point a).

It is fitted with:

- pin stopcock;

- a dial pressure gauge, in accordance with T.S. 9991308 "Measuring and precision indicating instruments for plant installations", Bourdon spring type, metal case, watertight for assembly in the field, with "gas" threaded connection UNI EN 10226 ND 1/2”, dial diameter 100 mm, with adequate full scale to allow easy and accurate reading of OPu, which must be between 25% ÷ 75% of full scale value, and maximum error not greater than 2.5% of full scale value.

- Pressure gauge intake for pressure control upstream of safety devices

This is positioned on each reduction line, immediately upstream of the safety devices; it is made as in point a) and may consist of the manometric device in point 5.2.2.

It is fitted with:

- pin stopcock;

- a dial pressure gauge, in accordance with T.S. 9991308 "Measuring and precision indicating instruments for plant installations", Bourdon spring type, metal case, watertight for assembly in the field, with "gas" threaded connection UNI EN 10226 ND 1/2”, dial diameter 100 mm, with adequate full scale to allow easy and accurate reading of OPu, which must be between 25% ÷ 75% of full scale value, and maximum error not greater than 2.5% of full scale value.

- Pressure gauge intake for intermediate pressure control between the pressure reducer-regulators with service and monitor function

This allows measurement of the intermediate pressure between the pressure reducer-regulator with monitor function and the pressure reducer-regulator with service function and has dimensions of at least ½" with "gas" threaded connection UNI EN 10226, positioned in front of the reduction line.

It is fitted with:

- pin stopcock;

- a dial pressure gauge, in accordance with T.S. 9991308 "Measuring and precision indicating instruments for plant installations", Bourdon spring type, metal case, watertight for assembly in the field, with threaded "gas" connection UNI EN 10226 ND 1/2", dial diameter 100 mm, with adequate full scale to allow easy and accurate reading of OPu, which must be between 25% ÷ 75% of full scale value, and maximum error not greater than 2.5% of full scale value; with minimum pressure index for storing any activations of the pressure reducer-regulator with monitor function.

- Pressure and impulse taps on the reduction line

They enable the operation of the line and its control.

- Pressure intake downstream of the pressure reducer-regulators.

Allows the measurement of pressure downstream of the pressure reducer-regulator with service function in the case of line exclusion for function and calibration checks and tests.

It is positioned on the section of pipe, downstream of the pressure reducer-regulator with service function and upstream of the shut-off valve of the reduction line; it is made as in point a) and must not be the impulse tap for operation of the regulation equipment and safety devices.

It is fitted with a pin stopcock, fitted with closing cap preferably connected to it by means of a chain.

- Pressure gauge intake for pressure control downstream of the pressure regulation system.

It is positioned immediately downstream of the pressure regulation system; it is made as in point a).

It is fitted with:

  - pin stopcock;

  - a dial pressure gauge, in accordance with T.S. 9991308 "Measuring and precision indicating instruments for plant installations", Bourdon spring type, metal case, watertight for assembly in the field, with threaded "gas" connection UNI EN 10226 ND 1/2”, dial diameter 100 mm, with adequate full scale to allow easy and accurate reading of OPd, which must be between 25% ÷ 75% of full scale value, and maximum error not greater than 2.5% of full scale value.

- Impulse tap for pressure reducer-regulators and blocking valve.

Low-pressure impulse taps are provided on the following equipment:

  - pressure reducer-regulator pilot with emergency function (monitor);

  - pressure reducer-regulator pilot with service function (where envisaged);

  - pressure reducer-regulator with a monitor function;

  - pressure reducer-regulator with a service function;

  - blocking valve;

- Regulated pressure control gauge intake

Allows the outlet pressure of the reduction line(s) to be measured. It is positioned downstream of the shut-off valve of the main line (on the downstream manifold) and is made as in point a) fitted with a closing cap preferably connected to it by means of a suitable chain, in a frontal or lateral position and not at the rear of the manifold and has dimensions of not less than ND ½" as a rule.

## Electrostatic discharge protection

In order to ensure protection against the build-up of electrostatic discharges, the reduction unit must be equipped with an earthing connection between the unit and a bolt anchoring the cabinet to the base.

This connection must be made with a yellow-green copper cable with a minimum cross-section of 4 mm2, PVC or G7 rubber insulated of an adequate length, fitted with cable lugs at the brass ends.

## Pipes, joints and special parts

The pipes, with related fittings, special parts and component materials, must comply with the requirements set out in the Ministerial Decree of 16 April 2008 and comply with the following specifications:

- T.S. 15AA300 “Welded steel pipes for natural gas pipelines”;

- T.S. 17AA300 “Steel fittings”.

They must also be suitable for the intended use in accordance with the regulations in force.

### Materials

The materials must be suitable for the intended use. The pipes with related fittings and special parts must be made of steel. The use of spheroidal cast iron is allowed.

Instrument connection tubes and impulse taps may be made of material other than steel, provided they are metallic (e.g. copper); they must be joined by welding or by suitable mechanical couplings.

### Joints

All connecting joints of the pipes with each other and with the equipment constituting the FRU must be designed and manufactured in such a way as to guarantee a perfect seal over time, even in the presence of vibrations and/or mechanical stresses to which the system elements may be subjected.

The number of threaded joints (which may never be used for pipes with ND50) must be kept to a minimum in order to reduce the possibility of leaks from the system. These joints must comply with UNI EN 10226. To ensure a better seal, hemp with suitable, long-lasting glues, polytetrafluoroethylene tape or other equivalent materials specifically declared suitable according to UNI EN 751-3 may be applied to the ends.

In order to limit micro-dispersion phenomena not detectable by instrumental tests, joints made with compression fittings must have equivalent sealing and reliability characteristics to those of ferrule fittings.

Welded connections must comply with standards and qualified procedures.

Flange joints must comply with applicable laws, directives and standards, taking into account the technical/construction characteristics of the individual piece of equipment.

These characteristics, which must be adhered to when selecting flanges, are indicated, where present, in the various chapters of this Technical Specification.

## Protective coating (painting)

Each FRU must be protected from external corrosion damage. Any metal surfaces to be painted must offer maximum adhesion to the protective film. To such purpose, they must be suitably subjected to treatment cycles so as to be cleaned of any foreign matter (e.g. degreasing, mechanical cleaning, etc.) that prevents adherence of the paint, guaranteeing suitable characteristics for the type of product.

The following characteristics are therefore required:

- high coefficient of adhesion to the surface to be protected;

- good anti-corrosion properties;

- reduced porosity and permeability to gases and liquids;

- resistance to the persistent action of atmospheric and chemical agents;

- colour = RAL 1016 (yellow).

# Marking

On each FRU an identification plate must be affixed in an easily identifiable and readable position, indicating the data as provided for by point 3.3, letter a) of Annex I to Legislative Decree no. 93 of 25 February 2000 as amended and supplemented by the following information:

- Type of "Final Reduction Unit" (Supplier's ref.);

- Maximum upstream operating pressure (MOPu);

- Maximum downstream operating pressure (MOPu);

- Design pressure (DP);

- Upstream operating pressure (OPu);

- Nominal flow rate (Qnom);

- Maximum flow rate (Qmax);

- Year of construction;

- Weight in kilograms;

- Serial number or other identification data of the Final Reduction Unit;

- Serial number of the control system;

- Purchase order number and position.

Similarly, on each main piece of equipment composing the FRU – such as valves, filters, blocking valves, pressure reducer-regulators, pilots, atmosphere release devices etc. – an identification plate must be affixed containing, as a minimum requirement, the following data:

- Manufacturer's name and/or trademark;

- Type and model of equipment;

- Year of construction;

- Features (see Supplier's);

- Serial number or other identifying data;

- Pressures (max. supply, operating, flanging, etc.);

- Nominal flow rate expressed in Sm3/h:

- Calibration range;

- Operating temperature range;

- Any references for spare parts (e.g. filter cartridge, etc.).

# MACHINING TOLERANCES

The system of tolerances and couplings envisaged, except where design and processing requirements require specific tolerances, must comply with the following standards:

UNI EN 22768 parts 1 and 2, or equivalents;

UNI EN 286 Parts 1 and 2, or equivalents.

# HOUSING

The housing must be constructed of materials with a reaction to fire rating not greater than 1, see Ministerial Decree of 26 June 1984 and subsequent amendments (e.g. galvanised sheet metal, fibreglass cabinet, etc.), provided it is designed in such a way as to give the structure good stability characteristics against adverse weather conditions (snow, wind, etc.).

Since there is no personnel access inside the cabinet, at least one of the walls must be completely removable or openable to the outside with doors fitted with a VIRO 8211 latch lock with F33642 key, in order to allow manoeuvring, checks and normal maintenance operations.

Ventilation must be provided by means of unobstructed openings having a surface area of at least 20% of the floor surface.

The openings are to be made in the walls, partly at the top and partly at the bottom and opposite each other. In addition, they may be made without rain deflectors in compliance with the presence of free openings, protected with fireproof netting.

Door leaves, if they have a surface area greater than 0.5 m2, must be fitted with a blocking system in the open position.

If it is necessary to install RTUs for the control of the supply pressure and regulation of the FRU, appropriate fastening devices must be provided, located inside the side wall of the cabinet, which do not obstruct the monitoring and maintenance of the equipment constituting the FRU.

The maximum dimensions of the cabinets, expressed in millimetres, must be as shown for Meshed FRUs in Table 5 and for Antenna FRUs in    Table 6:

Table 5: Cabinets for meshed FRUs				Table 6: Cabinets for Antenna FRUs

| System code | MAXIMUM CABINET DIMENSIONS |  |
| --- | --- | --- |
|  | LENGTH mm | WIDTH mm |
| FRU 1/M | 1600 | 800 |
| FRU 2/M | 1600 | 800 |
| FRU 3/M | 1600 | 800 |
| FRU 4/M | 2100 | 1000 |
| FRU 5/M | 2400 | 1200 |
| FRU 6/M | 2800 | 1200 |

| System code | MAXIMUM CABINET DIMENSIONS |  |
| --- | --- | --- |
|  | LENGTH mm | WIDTH mm |
| FRU 1/A | 1600 | 900 |
| FRU 2/A | 1600 | 900 |
| FRU 3/A | 1600 | 1000 |
| FRU 4/A | 2100 | 1200 |
| FRU 5/A | 2400 | 1350 |
| FRU 6/A | 3000 | 1550 |

# ABATEMENT OF ACOUSTIC EMISSIONS

In relation to the need to install final reduction units in compliance with the legal provisions in force, regarding noise pollution of the environment (noise emissions), they must comply, by means of the expedients deemed most suitable by the supplier (e.g. silent pressure reducers-regulators, soundproof cabinets, etc.) with the following maximum permissible noise emission levels under conditions of maximum output:

Table 7: Noise emissions for standard FRUs

| - Noise emission levels of FRUs under standard conditions |  |
| --- | --- |
| - Distance from cabinet walls: 2 m | - Distance from cabinet walls: 10 m |
| - dB(A) = 65 | - dB(A) = 55 |

Although the above is not the standard solution, Italgas Reti may specifically request, with a separate quotation to be indicated in the offer phase, the supply of plants meeting more stringent noise emission levels indicated below, depending on the requirements imposed by current legislation.

Table 8: Noise emissions for non standard FRUs

| - Noise emission level of FRUs under non standard conditions |  |
| --- | --- |
| - Distance from cabinet walls: 2 m | - Distance from cabinet walls: 10 m |
| - dB(A) = 50 | - dB(A) = 45 |
| - dB(A) = 45 | - dB(A)  40 |

# TYPE TEST

During the design phase of the FRU, it will be the Supplier's responsibility to carry out at recognised laboratories or directly at the Supplier's premises all the "Type Tests" envisaged by the reference standards and/or the Supplier's own design standards and the standards referred to therein to verify the intended end use of the FRU.

Note:

Type tests are not envisaged in the event that Italgas Reti deems that any modifications made by the Supplier to the FRUs already accepted for company use, affecting the structure and/or the arrangement of the piping connecting the equipment, do not affect the functionality, safety and reliability of the FRU.

# DOCUMENTATION required from the supplier

## Supplier

- The potential Supplier must be qualified as an ITALGAS RETI Supplier and must be able to provide after sales services directly in Italy.

## Documentation for the company approval process

The potential Supplier must submit the following documentation to the PROMA-CMMAT Department at the tender stage:

- “Declaration of conformity” with this technical specification and any specific documents mentioned in it (legal provisions, applied standards, MID Directive, ATEX, EMC, PED, etc.) to which the supplier refers for the design and construction of the product, as indicated in the UNI CEI EN ISO/IEC 17050-1 standard (see the example given in APPENDIX 1 of this technical specification);

In addition, the SERTEC-NORM Department of Italgas Reti, may request the schematic drawings of the FRUs showing the general dimensions and identifying characteristics of the main materials from the Supplier, upon completion of the tender process with awarding of the Supply Contract.

## Test Documentation

The Supplier must issue a “type 3.1” Inspection and Material Certificate in accordance with UNI EN 10204, stating that the FRU supplied are compliant with the requirements of these specifications as well as the legislative provisions as per point 14.

In accordance with UNI 8827, the Supplier must also produce a test report for each of the tests containing at least the following information:

- Name of the authorised person responsible for the test;

- Test date;

- System manufacturer;

- Identification of the section to which the test relates;

- Design pressure;

- Pressure reached during the test and the period of time for which it was maintained;

- Test fluid;

- Test results;

- Reference to the test procedure (if any);

- Instrumentation used for the test with indication of calibration validity;

- Type and serial number of the instrument used for the test.

Registration of the full production/test documentation completed by the Supplier must be kept (on the basis of legal provisions) for 10 years under its responsibility, and must be made available whenever requested by the Client.

## Supply Documentation

- Documents compliant with Legislative Decree no. 286 of 21 November 2005, as amended.

In addition, for each individual FRU, upon delivery the Supplier must provide to the DESTINATION UNIT a technical file (Data Book) containing at least the following documentation:

- “Type 3.1” Inspection and Material Certificates in accordance with UNI EN 10204;

- Statement certifying ownership to market the product;

- "EU Declaration of Conformity" in accordance with recent legislative decrees implementing the Directives applicable to the product (e.g. ATEX, PED Directives etc.).

- If, on the basis of the design of a project intended for use under pressure (Directive EU 68/2014), the Supplier determines that it does not fall within the characteristics defined by the aforementioned Directive, it must in any case submit a declaration of inclusion in Article 3, subsection 3 of the aforementioned Directive, certifying the exemption of the component in compliance with the provisions of such subsection (see the example in Appendix 2 to this Technical Specification).

- If, on the basis of the design of an FRU intended for use in potentially explosive atmospheres (Directive 2014/34/EU), the Supplier determines that its component does not fall within the scope of the aforementioned Directive, the Supplier must submit a declaration of assumption of responsibility (see the example in Appendix 3 of this T.S.) which certifies that, following the risk analysis carried out, the component does not have any potential ignition sources of its own, and therefore does not fall within the scope of Legislative Decree no. 85/2016 (Directive 2014/34/EU) and can therefore be installed in all the zone types referred to in Legislative Decree no. 233/03 (Directive 1999/92/EC);

- Any list of references of the main customers using the proposed materials;

- Copy of the "EU type inspection certificate" for products for which the applied directives require the intervention of a Notified Body (e.g. ATEX);

- User and maintenance manual in Italian which, for pressure equipment, complies with points 3.3 and 3.4 of Annex I to Legislative Decree no. 93 of 25 February 2000, as amended;

- Functional diagram, construction drawing and equipment list with materials used;

- Recommended spare parts list of equipment subject to preventive maintenance;

- Test report;

- Declaration of conformity and compliance with applicable UNI standards (e.g. UNI 8827);

- Declaration of conformity with applicable legislation;

- Declaration of conformity of installed equipment with applicable directives;

- Whatever else the potential Supplier considers useful to better qualify the proposed product.

- For equipment covered by the PED Directive 2014/68/EU (e.g. filters), for which at least two of the following conditions arise:

    - Internal diameter in mm or nominal dimensions 500 or less;

    - Maximum allowed pressure AP 6 bar or less;

    - The product of the internal diameter in mm or nominal dimensions ND times the maximum allowed pressure 3000 or less,

the Supplier must make available the documentation containing the basic data and construction characteristics (e.g. thicknesses) required to carry out integrity checks of the various components (external equipment body, ellipsoidal caps, etc.) of the pressure equipment.

# Tests and inspections

Italgas Reti reserves the right:

- To be present with its own Inspectors and/or Inspection Companies appointed by the same to carry out tests/checks c/o your plant and at your care and expense, to check the constructive and functional compliance of the materials in accordance with the specifications and/or reference standards.

- To verify, upon receipt and/or under actual conditions of use, the perfect compliance of the goods with the functional technical characteristics expressly indicated in the Contract.

It is understood that the favourable outcome of our inspection and checking of the materials shall not release you in any way from the responsibilities and obligations arising from each individual contract.

The tests and inspections described must be carried out by the Supplier on each FRU supplied:

- Visual and dimensional inspection (point 12.1);

- Mechanical strength test (point 12.2);

- Pneumatic external leak test (point 12.3);

- Functional tests (point 12.4);

- Non-destructive testing of welds (point 12.5).

## Visual and dimensional inspection

The construction and dimensional conformity with the construction drawing must be checked.

The dimensional tolerances of the threads must be those specified in the relevant standards.

The inspections must be certified in accordance with UNI EN 10204 type 3.1.

## Mechanical strength test

Before the installation is assembled, the main circuit of each FRU must undergo a mechanical strength test at the factory, which must be recorded. Test procedures must be chosen according to UNI EN 12327.

The mechanical strength test must have a minimum duration of 4 hours, after temperature stabilisation, and must be performed under the conditions specified below in Table 9:

Table 9: Mechanical strength test pressures

| Test pressure Pcol | MOP |
| --- | --- |
| 2.5 bar | MOP ≤ 1.5 bar (part affected by downstream pressure) |
| 7.5 bar | 1.5 < MOP ≤ 5 bar (part affected by upstream pressure) |

The test can be performed by means of a hydraulic test or by using air or inert gases.

The mechanical strength test is not required for:

- Pressure reducer-regulator, blocking valve, filter

for which the factory test must be carried out in accordance with the relevant regulations in force and in any case with a test pressure not lower than the values indicated in Table 9.

If the Supplier can prove, by means of suitable existing documentation, that the components of the main circuit have been previously tested at least to the required test pressure, the strength test need not be repeated on these components.

## Pneumatic external leak test

After the strength test, all the components that were removed from the installation before the test must be reinstalled.

The entire installation must be subjected to an external pneumatic leak test. The test must have a minimum duration of 30 minutes, after temperature stabilisation, and must be carried out under the following conditions:

- Upstream section: maximum operating pressure;

- Downstream section: 0.10 bar.

Air or inert gas or mains gas must be used as the test fluid.

The perfect tightness of the pressure reducer-regulator obturators and safety devices must also be checked and guaranteed by means of a pneumatic leak test, to be carried out for one minute immediately after the obturator has closed.

## Functional tests

The following functional tests must be carried out on each fully assembled FRU and must be certified in accordance with UNI EN 10204 type 3.1:

### Check calibration of the regulation pressure of the pressure reducer-regulator with service function

With reference to point 5.2.4.2 above, the value of the regulation pressure must comply with the order specifications and must be within the following tolerance values:

± 5 %. for piloted pressure reducer-regulators;

± 10% for direct-acting pressure reducer-regulators.

### Check regulation pressure with zero flow

The regulated pressure with zero flow must not exceed 120% of the regulated pressure during normal delivery; this condition must be checked with inlet pressures of either 0.5 bar or 5 bar.

### Check regulation pressure and triggering of pressure reducer-regulator with emergency function (monitor)

In addition to the tests referred to in points 12.4.1 and 12.4.2 above, triggering of the monitor within 10 seconds after the triggering pressure plus 5% is reached must be checked.

### Check triggering of the relief device

By gradually increasing the regulation pressure, the relief device must trigger when the pressure set by the pressure reducer-regulator with monitor function is exceeded and before the downstream maximum pressure blocking valve, if any, is triggered.

The test can be performed by artificially increasing the pressure, by means of suitable equipment external to the plant.

### Check calibration of the maximum regulation pressure blocking valve

The check must be carried out by varying the regulation pressure, as described in point 12.4.4 above, until the delivery blocking valve(s) is/are triggered. This test must be repeated six consecutive times. The values found must be within the tolerance of ±10%.

## Non-Destructive Testing (NDT) of welds

Welding of steel pipes must be carried out in accordance with UNI EN 12732, according to qualified procedures complying with UNI EN ISO 15614-1 or equivalent standards.

Welders must be qualified in compliance with UNI EN ISO 9606-1 or equivalent standards.

The Supplier must carry out non-destructive testing of the welds of the  plants at its own expense, in accordance with the relevant UNI standards.

All non-destructive testing operations must be carried out by qualified Level 2 personnel in accordance with formalised procedures. Level 2 personnel must be certified in compliance with UNI EN ISO 9712.

The non-destructive testing (NDT) to be carried out on welded joints subjected to pressure must include at least the following checks:

- head-to-head welds must be radiographed at 20% in accordance with Italgas Reti and in compliance with UNI EN ISO 17636-1 (Class B); the acceptability level is level 1 according to UNI EN ISO 10675-1;

- any welds that cannot be radiographed must be checked 100% with liquid penetrants in accordance with UNI EN ISO 3452-1, acceptability level 1 to UNI EN ISO 23277 or with magnetic particles in accordance with UNI EN ISO 17638, acceptability level 1 according to UNI EN ISO 23278.

## Right of the client

It is Italgas Reti's right, for each purchase order, to request from the Supplier:

- Further technical and/or graphic documentation,

- additional laboratory and/or field tests,

in order to verify the conformity of the proposed products with this technical specification and the cited standards to which reference is made.

# Conditions of Supply

The reduction plants must be supplied pre-assembled on a metal skid suitably designed and manufactured to allow and facilitate the manoeuvring of the shut-off devices as well as control and maintenance operations of the filtration, regulation and safety equipment.

The arrangement of the equipment must be such as to allow for the proper functioning of the reduction unit. The maximum height of the pre-assembled reduction unit should not exceed h max = 1.9 m from the floor. The equipment must be assembled according to good engineering practice. In particular, the layout of the pipes must not give rise to additional stresses on the equipment connected to them.

## Packaging

Potential Supplier's standard in compliance with Legislative Decree no. 152 of 3 April 2006 as amended and supplemented.

# REFERENCE STANDARDS

- Law 26/10/95 no. 447 “ Framework Law on Noise Pollution".

- Legislative Decree No. 85 of 19 May 2016 - “Implementation of Directive 2014/34/EU on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres”.

- Italian Legislative Decree no. 93 of 25 February 2000, as amended - Implementation of Directive 97/23/EC on pressure equipment and Directive 2014/68/EU on the harmonisation of the laws of the Member States relating to the making available on the market of pressure equipment (recast), providing for its repeal.

- Legislative Decree No. 233 of 12 June 2003 “Implementation of Directive 1999/92/EC on minimum requirements for improving the safety and health protection of workers exposed to the risk of explosive atmospheres”.

- Italian Legislative Decree no. 152 of 03 April 2006, as amended “Environmental standards”.

- Italian Legislative Decree no. 81 of 09 April 2008, as amended “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”.

- Ministerial Decree of 19 February 2007 "Approval of the technical regulation on the chemical-physical characteristics and presence of other components in combustible gas to be transported".

- Ministerial Decree of 16 April 2008 “Technical regulations for the design, construction, testing, operation and supervision of works and distribution systems and direct lines for natural gas with a density not exceeding 0.8”.

- Ministerial Decree 26 June 1984, as amended – "Classification of reaction to fire and approval of materials for the purposes of fire prevention".

- UNI 8827 "Gas pressure control systems operating with upstream pressure between 0.04 bar and 5 bar - Design, construction and testing".

- UNI 9165 “Gas distribution networks - Pipeworks with maximum operating pressure up to 5 bar - Design, construction, testing, operation, maintenance and rehabilitation”.

- UNI 11354 "Shut-off devices for gas distribution and/or transportation networks - Butterfly valves”;

- UNI 9734 “Shut-off devices for gas pipelines. Steel valves with ball obturator”.

- UNI 10285 "Monolithic insulation joints. 80 ≤ ND ≤ 600. NP 16".

- UNI CEI EN ISO/IEC 17050-1 - "Conformity assessment - Supplier's declaration of conformity - Part 1: General requirements”.

- UNI CEI EN ISO/IEC 17050-2 - "Conformity assessment - Supplier's declaration of conformity - Part 2: Supporting documentation".

- UNI EN 1555-2 “Plastic piping systems for the supply of gaseous fuels - Polyethylene (PE) - Part 2: Pipes”.

- UNI EN 12186 "Gas infrastructure - Gas pressure regulating stations for transport and distribution - Functional requirements".

- UNI EN 12327 "Gas infrastructures - Pressure testing, commissioning and decommissioning procedures for gas supply networks - Functional requirements".

- UNI EN 12732 "Gas infrastructures - Welding of steel pipework - Functional requirements".

- UNI EN 10204 “Metallic products - Types of inspection documents”.

- UNI EN 10226 “Pipe threads for thread seal coupling”.

- UNI EN 751-3 "Sealing material for metallic threaded joints in contact with 1st, 2nd and 3rd family gases and hot water - Unsintered PTFE tapes".

- UNI EN 334 "Gas pressure regulators for inlet pressures up to 100 bar".

- UNI EN 12279 "Transport and distribution of gas - Gas pressure regulating installations on distribution networks - Functional requirements"

- UNI EN ISO 22768-1 "General tolerances. Tolerances for linear and angular dimensions without tindividual tolerance indications"

- UNI EN ISO 22768-2 "General tolerances. Geometric tolerances for features without individual tolerance indications"

- UNI EN ISO 3452-1 “Non-destructive testing - Penetrant testing - Part 1: General Principles”.

- UNI EN ISO 23277: “Non-destructive testing of welds - Penetrant testing - Acceptance levels".

- UNI EN ISO 17638: "Non-destructive testing of welds - Magnetic particle testing".

- UNI EN ISO 23278: "Non-destructive testing of welds - Magnetic particle testing - Acceptance levels".

- UNI EN ISO 17636-1 "Non-destructive testing of welds - Radiographic testing - Part 1: X and gamma-ray techniques with film".

- UNI EN ISO 10675-1 "Non-destructive testing of welds - Acceptance levels for radiographic inspection - Part 1: Steel, nickel, titanium and their alloys".

- UNI EN ISO 9712 "Non-destructive testing - Qualification and certification of non-destructive testing personnel"

- UNI EN ISO 15614-1 “Specification and qualification of welding procedures for metallic materials - Welding procedure test - Part 1: Arc and gas welding of steels and arc welding of nickel and nickel alloys”.

- UNI EN ISO 286-1 "Geometrical product specifications (GPS) - ISO code system for tolerances on linear sizes - Part 1: Fundamental principles for tolerances, deviations and fits”.

- UNI EN ISO 286-2 "Geometrical product specifications (GPS) - ISO code system for tolerances on linear sizes - Part 2: Tables of standardised tolerance classes and limit deviations of holes and shafts".

- UNI EN ISO 3183 - “Petroleum and natural gas industries - Steel pipe for pipeline transportation systems”.

# ATTACHMENTS

- Annex 1 – T.S. 23273. "List of pressure reducers-regulators approved for company use”.

- Annex 2 - Table M. 17850 "Steel dielectric joint, NP 16, butt-weld ends"

- Annex 3 – T.S. 1800300 “Polyethylene fittings and special parts”.

- Annex 4 – T.S. 2000300 “Steel valves for gas pipelines”.

- Annex 5 – T.S. 9991300 - "Cartridge filter elements for filters of gas reduction and metering units and plants".

- Annex 6 – T.S. 15AA300 “Welded steel pipes for natural gas pipelines”.

- Annex 7 – T.S. 17AA300 “Steel fittings”.

- Annex 8 – T.S. 9991308 "Measuring and precision indicating instruments for plant installations".

# Appendices

- APPENDIX 1 - “Sample declaration of conformity with this technical specification”

- APPENDIX 2 – “Sample declaration of SOUND ENGINEERING PRACTICE (SEP)”

- APPENDIX 3 – “Sample declaration of ATEX Exclusion”.

## Appendix 1

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN ISO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

(4)	The following products manufactured by us:

| Our material code (5) | Italgas Reti material code (6) |
| --- | --- |
| xxx | 2327920 |

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(7)	T.S. F.C. 2327300	Final reduction units from road pipes	Edition 2 of 15/06/2017

with upstream pressure connection between 0.5 and 5 bar

Additional information:

(8) 	...................................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(9) 	............................................................. 			......................................................................................................................

(Name and position) 						(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- The “subject” must be unambiguously described so that the declaration of conformity can be referred to the subject in question.

- List all the products for which company use authorisation is being requested.

- For each individual product supplied, state the material code used by the Supplier.

- For each individual product supplied, please quote the material code assigned by Italgas Reti, which can be found in the Italgas Reti reference documents. If there are none, please contact SERTEC-NORM.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

## Appendix 2

Declaration of compliance with Article 3, subsection 3 of Legislative Decree no. 93

(SEP Declaration)

We ..............................................................................................................................................................

(name of organisation)

with registered office in .............................................................................................................

(address)

as the .................................................................................................................................................

(Manufacturer / Authorised Representative)

we declare that, following the analysis carried out in accordance with Legislative Decree no. 26 of 15 February 2016 implementing the Integration Directive 2014/68/EU,

the series products:

..................................................................................................................................................................... ..................................................................................................................................................................... (name, type or model, batch, group or serial number)

described in the document:

…………………..………..……………………………………………………………………………….

…………………..………..……………………………………………………………………………….

(title and/or number and date of publication of the Standard(s) or other regulatory document(s))

to which this declaration refers, fall under Article 3, subsection 3 of Legislative Decree no. 93 of 25 February 2000 as amended, and are therefore subject to the provisions thereof. Consequently, the products mentioned are not subject to CE marking for the application of Legislative Decree no. 93 of 25 February 2000 as amended.

## Appendix 3

ATEX Exclusion Declaration

We ..............................................................................................................................................................

(name of organisation)

with registered office in .............................................................................................................

(address)

as the .................................................................................................................................................

(Manufacturer / Authorised Representative)

declare under our sole responsibility that the products series

.....................................................................................................................................................................

.....................................................................................................................................................................

(name, type or model, batch, group or serial numbers)

described in the Technical Specification / document(s)

.....................................................................................................................................................................

.....................................................................................................................................................................

(when necessary)

to which this declaration refers, comply with the following legislative / regulatory document(s)

.....................................................................................................................................................................

.....................................................................................................................................................................

(title(s) and/or number(s) and date(s) of publication of the standard(s) or other legislative and/or regulatory document(s))

and, according to Article 1, subsection 1a) of Directive 2014/34/EU of 26 February 2014 (Legislative Decree no. 85 of 19 May 2016) and Chapter 1 of ATEX 2014/34/EU GUIDELINES (first edition), based on an ATEX analysis (see subsection 32 of the aforementioned ATEX 2014/34/EU GUIDELINES), do not fall within the scope of the Directive 2014/34/EU, as they do not risk causing an explosion due to the lack of potential ignition sources, as defined in Standard UNI EN 1127-1, when used in systems that comply with the following legislative and/or regulatory documents

.....................................................................................................................................................................

.....................................................................................................................................................................

.....................................................................................................................................................................

(title and/or number and date of publication of legislative and/or regulatory documents)

They can therefore be installed in all types of zones as defined in Legislative Decree no. 81 of 9 April 2008, as amended, Title XI (Directive 1999/92/EC of 16 December 1999).

..................................................................		..................................................................................................................................

(place and date of issue)		(name and signature or equivalent stamp of authorised person)

Henceforth referred to simply as FRU.

In the case of FRU in antenna (double line).

Aluminium alloys are not allowed.

Maximum permissible acoustic emission levels.

Supplier means the entity responsible for the design and construction of the products or its legal representative as defined in Legislative Decree no. 206 of 6 September 2005 as amended and supplemented - “CONSUMER CODE” pursuant to Article 7 of Law no. 229 of 29 July 2003.

DESTINATION UNIT means the OPERATIONAL UNIT receiving the FRU.

SOUND ENGINEERING PRACTICE