“TECHNICAL SPECIFICATION FOR EVALUATION, SUPPLY AND TESTING”

S.T.V.F.C. TC-1/631

Electronic measuring instruments, transducers and local calibration apparatus

| Compiled by | SERTEC-NORM | IRRERA, ANDREA |
| --- | --- | --- |
| Checked by | SERTEC-NORM | VARESE, ENRICO |
| Checked by | MISURA-SVILMIS | GHIA, SERGIO |
| Checked by | SERTEC-INTEC | ZAGATO, FULVIO |
| Checked by | PROMA/CMMAT | FASSINO, SILVIO |
| Checked by | PROMA-MATMA | SCOTTO, ENRICO |
| Checked by | SERTEC-LAB | SALATI, EUGENIO |
| Checked by | HSEQ | BOLZONI, GIANLUCA |
| Approved by | SERTEC | COMAZZI, MARCO |

SUMMARY

1	PRELIMINARY INFORMATION	4

1.1	Cancels and replaces	4

1.2	Reason for issue	4

1.3	Company departments mentioned in the document	4

1.4	Definitions	4

2	PURPOSE AND FIELD OF APPLICATION	5

2.1	Purpose	5

2.2	Field of application	5

3	SPECIFICATIONS	5

4	TECHNICAL CHARACTERISTICS	5

4.1	"SMART" electronic differential pressure transmitter – TPD1	7

4.1.1	Mechanical characteristics	7

4.1.2	Electrical characteristics	7

4.1.3	Application	8

4.2	"SMART" electronic differential pressure transmitter – TPD2	9

4.2.1	Mechanical characteristics	9

4.2.2	Electrical characteristics	9

4.2.3	Application	10

4.3	"SMART" electronic absolute pressure transmitter– TPA1	11

4.3.1	Mechanical characteristics	11

4.3.2	Electrical characteristics	11

4.3.3	Application	12

4.4	"SMART" electronic absolute pressure transmitter– TPA2	13

4.4.1	Mechanical characteristics	13

4.4.2	Electrical characteristics	13

4.4.3	Application	14

4.5	"SMART" electronic relative pressure transmitter – TPR1	15

4.5.1	Mechanical characteristics	15

4.5.2	Electrical characteristics	15

4.5.3	Application	16

4.6	"SMART" electronic relative pressure transmitter – TPR2	17

4.6.1	Mechanical characteristics	17

4.6.2	Electrical characteristics	17

4.6.3	Application	19

4.7	"SMART" electronic temperature transmitter - TT	20

4.7.1	Mechanical characteristics	20

4.7.2	Electrical characteristics	20

4.7.3	Application	21

4.8	Thermoresistance Pt 100 – RTD	22

4.8.1	Mechanical characteristics	22

4.8.2	Electrical characteristics	22

4.8.3	Application	22

4.9	Electro-Pneumatic Transducer - TEP	24

4.9.1	Mechanical characteristics	24

4.9.2	Electrical characteristics	24

4.9.3	Application	25

4.10	Portable local calibration equipment for "SMART" type transmitters	26

4.10.1	Mechanical characteristics	26

4.10.2	Electrical characteristics	26

4.10.3	Application	27

4.11	Technical assessment	27

5	Marking	27

6	TYPE TEST	27

7	DOCUMENTATION REQUIRED FROM THE SUPPLIER	28

7.1	Supplier	28

7.2	Documents to be submitted	28

7.3	Test Documentation	28

7.4	Supply Documentation	29

8	TESTS AND INSPECTIONS	29

8.1	Right of the Client	29

9	CONDITIONS OF SUPPLY	29

10	REFERENCE STANDARDS	30

11	APPENDICES	31

APPENDIX 1	32

# PRELIMINARY INFORMATION

## Cancels and replaces

This specification cancels and replaces the following Technical Specifications:

- Specification 631 – "Electronic differential pressure transmitter class 0.1 SMART compliant with Ex-i design", Edition no. 1, Revision 0 of 29 October 1996.

- Specification 632 – "Electronic absolute pressure transmitter (PT)", Edition no. 1, Revision 0 of 29 October 1996.

- Specification 633 – "Electronic temperature transmitter class 0.1 "SMART" -10°C + 40°C compliant with Ex-i design", Edition no. 1, Revision 0 of 29 October 1996.

- Specification 634 – "Thermoresistance PT 100 -10°C  ÷ +40°C unified for AD-PE or AD-I plants", Edition no. 1, Revision 0 of 29 October 1996.

- Specification 636 – "Electropneumatic transducer 4 ÷ 20 mA / 3 ÷ 15 p.s.i. compliant with Ex-i design", Edition no. 1, Revision 0 of 29 October 1996.

- Specification 637 – "Specification Electronic Relative Pressure Transmitter (PT) class 0.1 "SMART" compliant with Ex-i design", Edition no. 1, Revision 0 of 29 October 1996.

- Specification 638 – "Specification Electronic Relative Pressure Transmitter (PT) class 0.25 "SMART" compliant with Ex-i design", Edition no. 1, Revision 0 of 29 October 1996.

- Specification 642 – "Electronic differential pressure transmitter class 0.25 "SMART" compliant with Ex-i design", Edition no. 1, Revision 0 of 29 October 1996.

- Specification 643 – "Portable local calibration apparatus compliant with Ex-i for "SMART" type transducers", Edition no. 1, Revision 0 of 29 October 1996.

## Reason for issue

The update and incorporation of Specifications 631, 632, 633, 634, 636, 637, 638, 642 and 643 and their reissue in the form of Technical Specifications for Assessment, Supply and Testing (S.T.V.F.C.), became necessary as a result of:

- new legislative context;

- issuing of new national and European standards (e.g. UNI, CEI, EN, etc.);

- inclusion of Supply and Testing Criteria;

- new company choices.

## Company departments mentioned in the document

- SERTEC-NORM = Standard

- PROMA-CMMAT = Category Manager Materials of Italgas S.p.A.

## Definitions

For definitions of the technical terms used in this specification, please refer to the relevant regulations, a non-exhaustive list of which can be found in Chapter 10.

# PURPOSE AND FIELD OF APPLICATION

## Purpose

The purpose of this T.S. is to define the technical and constructional characteristics, the accompanying documentation and the procedures for carrying out the technical inspections to be performed for approval for company use of electronic measuring instruments, transducers and local calibration apparatus for "SMART" type electronic transmitters.

## Field of application

This Technical Specification applies, in the case of direct purchase by Italgas Reti, whenever a material covered by this specification must be approved for company use, produced by a new potential Supplier or by an existing Supplier.

# SPECIFICATIONS

- These technical specifications must be understood as an integral part of the "ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS."

- This specification contains the minimum technical requirements demanded by Italgas Reti based on the reference legislative and technical standards.

- It is the Supplier's responsibility to ensure that the products supplied fully comply with the provisions of this technical specification and the applicable standards.

- If the materials in question are supplied by an installer, the installer must document their compliance as required under “Documentation required from the Supplier”.

- It is the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. sharp edges or incorrect directions for use and maintenance), which may jeopardise the health and safety of the Client's workers in relation to the provisions of Italian Legislative Decree no. 81/08, as amended and supplemented.

- For any technical and operational aspects that conflict with or are not mentioned in this technical specification but that nevertheless pertain to the design, installation, maintenance and use of the products themselves, it is the Supplier's responsibility to refer to the regulations in force.

# TECHNICAL CHARACTERISTICS

The electronic measuring instruments, transducers and local calibration apparatus for "SMART" type electronic transmitters, covered by this Technical Specification, are subject to Law no. 186/68, relating to the realisation and construction of materials, equipment, machinery, installations and electrical and electronic systems “to standard”; they must therefore be suitable for their intended use and ensure, as regards the materials used and their construction, adequate resistance to the environmental and mechanical factors to which they may be exposed during operation.

They are also subject to a whole series of legislative provisions, in relation to the required characteristics, materials and intended use, a non-exhaustive list of which is provided in Chapter 10 of this T.S.

Unless explicitly referred to otherwise, the standards cited are those in the latest edition, including any variants/updates and/or corrigenda published.

The types of electronic measuring instruments and transducers covered by this T.S. are summarised in the table below:

| Instrument | Type | Accuracy reference |
| --- | --- | --- |
| "SMART" electronic differential pressure transmitter | TPD1 | ± 0.1 % |
| "SMART" electronic differential pressure transmitter | TPD2 | ± 0.25 % |
| "SMART" electronic absolute pressure transmitter | TPA1 | ± 0.1 % |
| "SMART" electronic absolute pressure transmitter | TPA2 | ± 0.25 % |
| "SMART" electronic relative pressure transmitter | TPR1 | ± 0.1 % |
| "SMART" electronic relative pressure transmitter | TPR2 | ± 0.25 % |
| "SMART" electronic temperature transmitter | TT | (1) |
| Thermoresistance Pt 100 | RTD | Class A |
| Electric-pneumatic transducer 4 ÷ 20 mA / 3 ÷ 15 psi | TEP | ± 0.5 % |

Table 1: Types of electronic measuring instruments and transducers

Notes:

- Reference accuracy is the sum of digital accuracy and D/A.

The technical features (i.e. mechanical and electrical characteristics) of the electronic pressure and temperature transmitters, the Pt 100 thermoresistance and the electric-pneumatic transducer of the portable local calibration apparatus for "SMART" type transmitters are indicated below.

## "SMART" electronic differential pressure transmitter – TPD1

The "SMART" electronic differential pressure transmitter must be an electrical device suitable for installation in "hazardous locations" (in relation to explosive gas atmospheres), in accordance with CEI EN 60079-10-1 and must belong to Group IIC intended for use in places with explosive atmospheres due to the presence of gas other than mines with possible presence of firedamp, have a temperature class T4 (min.), have a protection mode (or level) "ia" according to CEI EN 60079-0 and CEI EN 60079-11.

The electronic differential pressure transmitter must be provided with an EU type-test certificate in accordance with Directive 2014/34/EU, in which the input parameters of the transmitter are specified in order to enable the system designer to produce the intrinsically safe system description document in accordance with CEI EN 60079-14 and CEI EN 60079-25.

### Mechanical characteristics

The electronic differential pressure transmitter must have the following mechanical characteristics:

- Process fluid measured: natural gas.

- Reference accuracy (including hysteresis, linearity and repeatability): ± 0.1% of calibration SPAN or better.

- Zero elevation and suppression possible.

- Maximum static overpressure: 140 bar (min.) on both the H and L sides.

- Mounted on a 3-valve (or 5-valve) sealable manifold fitted with a vent valve, incorporated in the instrument itself, with 2 x ½" NPT-F process connections, and anti-condensation drums connected to each other and to the instrument via seamless stainless steel pipe and quality fittings.

- Threaded connections according to ASME B.1.20.1.

- Equipped with stainless steel mounting bracket for installation on 2" post.

- Protected against mechanical vibrations.

- Suitable for outdoor installation (≥ IP 65).

### Electrical characteristics

The electronic differential pressure transmitter must have the following electrical characteristics:

- Suitable for operation in an environment with temperatures between -20 °C and +75 °C, as a minimum.

- Output signal: 4  20 mA DC / two-wire HART (linear or square root).

- Power supply: 24 VDC 10% by means of a passive or active intrinsically safe barrier (see T.S. TC-1/561).

- Shielded against radio interference.

- Variable capacity operating principle with high-precision differential cell.

- Microprocessor with "SMART" functions suitable for portable local calibration equipment with features listed in point 4.10.

- Total response time: not exceeding 0.5 s.

- Damping: adjustable from 0 to 60 s.

- Possibility of calibrating the zero and SPAN of the instrument:

  - local calibration with direct access to the calibration system via keys located on the instrument without jeopardising the safety of the system;

  - digital portable calibration system suitable for use in both hazardous and non-hazardous locations, connectable at all points of the current loop. Digital communication between the transmitter and the portable calibration system should display instrument functionality, main characteristics and process data, without interrupting the 4  20 mA DC variable.

- Local measurement indication: via LCD display.

- Electrical connection: ISO M20 x 1.5.

- Intended for use in gas metering systems with venturimetric measurement with computer according to T.S. TC-1/682.

- Actual full scale (SPAN) to be chosen, when ordering, based on the operating pressure value using the expected possible scale range (RANGE) between 0 and 620 mbar with a minimum possible range between 0 and 21 mbar:

| REFERENCE | PRESSURE AT MEASUREMENT (barg) | Dp HIGH FLOW RATE FULL SCALE (mbar) | Dp LOW FLOW RATE FULL SCALE (mbar) |
| --- | --- | --- | --- |
| A | 0.5 to 3 | 200 | 50 |
| B | 3 to 5 | 200 | 50 |
| C | 3 to 5 | 200 | 50 - 80 - 100 |
| D | greater than 5 | 200 | 50 - 80 - 100 |

### Application

The electronic differential pressure transmitter can be used for the following applications:

- for venturimetric gas metering systems (ldpT-hdpT).

- in non-standard remote control applications.

## "SMART" electronic differential pressure transmitter – TPD2

The "SMART" electronic differential pressure transmitter must be an electrical device suitable for installation in "hazardous locations" (in relation to explosive gas atmospheres), in accordance with CEI EN 60079-10-1 and must belong to Group IIC intended for use in places with explosive atmospheres due to the presence of gas other than mines with possible presence of firedamp, have a temperature class T4 (min.), have a protection mode (or level) "ia" according to CEI EN 60079-0 and CEI EN 60079-11.

The electronic differential pressure transmitter must be provided with an EU type-test certificate in accordance with Directive 2014/34/EU, in which the input parameters of the transmitter are specified in order to enable the system designer to produce the intrinsically safe system description document in accordance with CEI EN 60079-14 and CEI EN 60079-25.

### Mechanical characteristics

The electronic differential pressure transmitter must have the following mechanical characteristics:

- Process fluid measured: natural gas.

- Reference accuracy (including hysteresis, linearity and repeatability): ±0.25% of calibration SPAN or better.

- Zero elevation and suppression possible.

- Maximum static overpressure: 130 bar (min.) on both the H and L sides.

- Mounted on a 3-valve (or 5-valve) sealable manifold fitted with a vent valve, incorporated in the instrument itself, with 2 x ½" NPT-F process connections, and anti-condensation drums connected to each other and to the instrument via seamless stainless steel pipe and quality fittings.

- Threaded connections according to ASME B.1.20.1.

- Equipped with stainless steel mounting bracket for installation on 2" post.

- Protected against mechanical vibrations.

- Suitable for outdoor installation (≥ IP 65).

### Electrical characteristics

The electronic differential pressure transmitter must have the following electrical characteristics:

- Suitable for operation in an environment with temperatures between -20 °C and +70 °C, as a minimum.

- Output signal: 4  20 mA DC / two-wire HART (linear or square root).

- Power supply: 24 VDC 10% by means of a passive or active intrinsically safe barrier (see T.S. TC-1/561).

- Shielded against radio interference.

- Diaphragm operating principle with variable capacitive cell.

- Microprocessor with "SMART" functions suitable for portable local calibration equipment with features listed in point 4.10.

- Total response time: not exceeding 0.5 s.

- Damping: adjustable from 0 to 60 s.

- Possibility of calibrating the zero and SPAN of the instrument:

  - local calibration with direct access to the calibration system via keys located on the instrument without jeopardising the safety of the system;

  - digital portable calibration system suitable for use in both hazardous and non-hazardous locations, connectable at all points of the current loop. Digital communication between the transmitter and the portable calibration system should display instrument functionality, main characteristics and process data, without interrupting the 4  20 mA DC variable.

- Local measurement indication: via LCD display.

- Electrical connection: ISO M20 x 1.5.

- Actual full scale (SPAN) to be chosen, when ordering, based on the operating pressure value using the possible scale ranges (RANGE( shown in the following table:

| REFERENCE | RANGE (mbar) | SPAN (mbar) | USE |
| --- | --- | --- | --- |
| A | 0 to 1 from 0 to 75 | 50 | ldpt |
| B | 0 to 65 from 0 to 370 | 50 80 100 200 | ldpt ldpt ldpt hdpt |
| C | 0 to 320 from 0 to 1800 | 500 600 | hdpt hdpt |

### Application

The electronic differential pressure transmitter can be used for the following applications:

- flow rate and volume measurements, but not for gas metering systems;

- local automatisms with no special precision requirements.

## "SMART" electronic absolute pressure transmitter– TPA1

The "SMART" electronic absolute pressure transmitter must be an electrical device suitable for installation in "hazardous locations" (in relation to explosive gas atmospheres), in accordance with CEI EN 60079-10-1 and must belong to Group IIC intended for use in places with explosive atmospheres due to the presence of gas other than mines with possible presence of firedamp, have a temperature class T4 (min.), have a protection mode (or level) "ia" according to CEI EN 60079-0 and CEI EN 60079-11.

The electronic absolute pressure transmitter must be provided with an EU type-test certificate in accordance with Directive 2014/34/EU in which the input parameters of the transmitter are specified in order to enable the system designer to produce the intrinsically safe system description document in accordance with CEI EN 60079-14 and CEI EN 60079-25.

### Mechanical characteristics

The electronic absolute pressure transmitter must have the following mechanical characteristics:

- Process fluid measured: natural gas.

- Reference accuracy (including hysteresis, linearity and repeatability): ±0.1% of calibration SPAN or better.

- Zero elevation and suppression possible.

- Maximum static overpressure: 140 bar (min.).

- Mounted on a 2-valve, sealable manifold fitted with a vent valve, incorporated in the instrument itself, with ½" NPT-F process connection, and anti-condensation drum connected to each other and to the instrument via seamless stainless steel pipe and quality fittings.

- Threaded connections according to ASME B.1.20.1.

- Equipped with stainless steel mounting bracket for installation on 2" post.

- Protected against mechanical vibrations.

- Suitable for outdoor installation (≥ IP 65).

### Electrical characteristics

The electronic absolute pressure transmitter must have the following electrical characteristics:

- Suitable for operation in an environment with temperatures between -20 °C and +75 °C, as a minimum.

- Output signal: 4  20 mA DC / two-wire linear HART.

- Power supply: 24 VDC  10% by means of a passive or active intrinsically safe barrier (see T.S. TC-1/561).

- Shielded against radio interference.

- Variable capacity operating principle with high-precision differential cell.

- Microprocessor with "SMART" functions suitable for portable local calibration equipment with features listed in point 4.10.

- Total response time: not exceeding 0.5 s.

- Damping: adjustable from 0 to 60 s.

- Possibility of calibrating the zero and SPAN of the instrument:

  - local calibration with direct access to the calibration system via keys located on the instrument without jeopardising the safety of the system;

  - digital portable calibration system suitable for use in both hazardous and non-hazardous locations, connectable at all points of the current loop. Digital communication between the transmitter and the portable calibration system should display instrument functionality, main characteristics and process data, without interrupting the 4  20 mA DC variable.

- Local measurement indication: via LCD display.

- Electrical connection: ISO M20 x 1.5.

- Intended for use in gas metering systems with venturimetric or volumetric measurement with computer according to T.S. TC-1/682.

- Actual full scale (SPAN) to be chosen, when ordering, based on the operating pressure value.

### Application

The electronic absolute pressure transmitter can be used for the following applications:

- transmitter for metering plant (TP).

## "SMART" electronic absolute pressure transmitter– TPA2

The "SMART" electronic absolute pressure transmitter must be an electrical device suitable for installation in "hazardous locations" (in relation to explosive gas atmospheres), in accordance with CEI EN 60079-10-1 and must belong to Group IIC intended for use in places with explosive atmospheres due to the presence of gas other than mines with possible presence of firedamp, have a temperature class T4 (min.), have a protection mode (or level) "ia" according to CEI EN 60079-0 and CEI EN 60079-11.

The electronic absolute pressure transmitter must be provided with an EU type-test certificate in accordance with Directive 2014/34/EU in which the input parameters of the transmitter are specified in order to enable the system designer to produce the intrinsically safe system description document in accordance with CEI EN 60079-14 and CEI EN 60079-25.

### Mechanical characteristics

The electronic absolute pressure transmitter must have the following mechanical characteristics:

- Process fluid measured: natural gas.

- Reference accuracy (including hysteresis, linearity and repeatability): ±0.25% of calibration SPAN or better.

- Zero elevation and suppression possible.

- Maximum static overpressure: 140 bar (min.).

- Mounted on a 2-valve, sealable manifold fitted with a vent valve, incorporated in the instrument itself, with ½" NPT-F process connection, and anti-condensation drum connected to each other and to the instrument via seamless stainless steel pipe and quality fittings.

- Threaded connections according to ASME B.1.20.1.

- Equipped with stainless steel mounting bracket for installation on 2" post.

- Protected against mechanical vibrations.

- Suitable for outdoor installation (≥ IP 65).

### Electrical characteristics

The electronic absolute pressure transmitter must have the following electrical characteristics:

- Suitable for operation in an environment with temperatures between -20 °C and +60 °C, as a minimum.

- Output signal: 4  20 mA DC / two-wire linear HART.

- Power supply: 24 VDC  10% by means of a passive or active intrinsically safe barrier (see T.S. TC-1/561).

- Shielded against radio interference.

- Diaphragm operating principle with variable capacitive cell.

- Microprocessor with "SMART" functions suitable for portable local calibration equipment with features listed in point 4.10.

- Total response time: not exceeding 0.5 s.

- Damping: adjustable from 0 to 60 s.

- Possibility of calibrating the zero and SPAN of the instrument:

  - local calibration with direct access to the calibration system via keys located on the instrument without jeopardising the safety of the system;

  - digital portable calibration system suitable for use in both hazardous and non-hazardous locations, connectable at all points of the current loop. Digital communication between the transmitter and the portable calibration system should display instrument functionality, main characteristics and process data, without interrupting the 4  20 mA DC variable.

- Local measurement indication: via LCD display.

- Electrical connection: ISO M20 x 1.5.

- Full scale to be chosen according to the measured pressure value so that the latter is between 60% and 90%.

### Application

The electronic absolute pressure transmitter can be used for the following applications:

- in non-standard remote control applications.

## "SMART" electronic relative pressure transmitter – TPR1

The "SMART" electronic relative pressure transmitter must be an electrical device suitable for installation in "hazardous locations" (in relation to explosive gas atmospheres), in accordance with CEI EN 60079-10-1 and must belong to Group IIC intended for use in places with explosive atmospheres due to the presence of gas other than mines with possible presence of firedamp, have a temperature class T4 (min.), have a protection mode (or level) "ia" according to CEI EN 60079-0 and CEI EN 60079-11.

The electronic relative pressure transmitter must be provided with an EU type-test certificate in accordance with Directive 2014/34/EU in which the input parameters of the transmitter are specified in order to enable the system designer to produce the intrinsically safe system description document in accordance with CEI EN 60079-14 and CEI EN 60079-25.

### Mechanical characteristics

The electronic relative pressure transmitter must have the following mechanical characteristics:

- Process fluid measured: natural gas.

- Reference accuracy (including hysteresis, linearity and repeatability): ±0.1% of calibration SPAN or better.

- Zero elevation and suppression possible.

- Maximum static overpressure: 140 bar (min.).

- Mounted on a 2-valve, sealable manifold fitted with a vent valve, incorporated in the instrument itself, with ½" NPT-F process connection, and anti-condensation drum connected to each other and to the instrument via seamless stainless steel pipe and quality fittings.

- Threaded connections according to ASME B.1.20.1.

- Equipped with stainless steel mounting bracket for installation on 2" post.

- Protected against mechanical vibrations.

- Suitable for outdoor installation (≥ IP 65).

### Electrical characteristics

The electronic relative pressure transmitter must have the following electrical characteristics:

- Suitable for operation in an environment with temperatures between -20 °C and +75 °C, as a minimum.

- Output signal: 4  20 mA DC / two-wire linear HART.

- Power supply: 24 VDC  10% by means of a passive or active intrinsically safe barrier (see T.S. TC-1/561).

- Shielded against radio interference.

- Variable capacity operating principle with high-precision differential cell.

- Microprocessor with "SMART" functions suitable for portable local calibration equipment with features listed in point 4.10.

- Total response time: not exceeding 0.5 s.

- Damping: adjustable from 0 to 60 s.

- Possibility of calibrating the zero and SPAN of the instrument:

  - local calibration with direct access to the calibration system via keys located on the instrument without jeopardising the safety of the system;

  - digital portable calibration system suitable for use in both hazardous and non-hazardous locations, connectable at all points of the current loop. Digital communication between the transmitter and the portable calibration system should display instrument functionality, main characteristics and process data, without interrupting the 4  20 mA DC variable.

- Local measurement indication: via LCD display.

- Electrical connection: ISO M20 x 1.5.

- Intended for use in gas metering systems with venturimetric or volumetric measurement with computer according to T.S. TC-1/682.

- Actual full scale (SPAN) to be chosen, when ordering, based on the operating pressure value using the possible scale ranges (RANGE( shown in the following table:

| REFERENCE | RANGE (bar) | SPAN (bar) | USE |
| --- | --- | --- | --- |
| A | 0 to 0.02 from 0 to 0.6 | 0.05 | LP MPA |
| B | 0 to 0.08 from 0 to 2.4 |  | MPB |
| C | 0 to 0.7 from 0 to 21 | 6 16 | PM UP - OP |
| D | 0 to 4.5 from 0 to 135 | 30 80 | UP - OP OP |
| E | from 0.2068428 to 1.034214 | 3 15 psi | PNEUMATIC SYSTEMS |

### Application

The electronic relative pressure transmitter can be used for the following applications:

- transmitter for metering plant (TP).

- remote control transmitter with ITALGAS REMOTE CONTROL system (PV-SV).

- transmitter for local automation or non-standard systems.

## "SMART" electronic relative pressure transmitter – TPR2

The "SMART" electronic relative pressure transmitter must be an electrical device suitable for installation in "hazardous locations" (in relation to explosive gas atmospheres), in accordance with CEI EN 60079-10-1 and must belong to Group IIC intended for use in places with explosive atmospheres due to the presence of gas other than mines with possible presence of firedamp, have a temperature class T4 (min.), have a protection mode (or level) "ia" according to CEI EN 60079-0 and CEI EN 60079-11.

The electronic relative pressure transmitter must be provided with an EU type-test certificate in accordance with Directive 2014/34/EU in which the input parameters of the transmitter are specified in order to enable the system designer to produce the intrinsically safe system description document in accordance with CEI EN 60079-14 and CEI EN 60079-25.

### Mechanical characteristics

The electronic relative pressure transmitter must have the following mechanical characteristics:

- Process fluid measured: natural gas.

- Reference accuracy (including hysteresis, linearity and repeatability): ±0.25% of calibration SPAN or better.

- Zero elevation and suppression possible.

- Maximum static overpressure: 140 bar (min.).

- Mounted on a 2-valve, sealable manifold fitted with a vent valve, incorporated in the instrument itself, with ½" NPT-F process connection, and anti-condensation drum connected to each other and to the instrument via seamless stainless steel pipe and quality fittings.

- Threaded connections according to ASME B.1.20.1.

- Equipped with stainless steel mounting bracket for installation on 2" post.

- Protected against mechanical vibrations.

- Suitable for outdoor installation (≥ IP 65).

### Electrical characteristics

The electronic relative pressure transmitter must have the following electrical characteristics:

- Suitable for operation in an environment with temperatures between -20 °C and +75 °C, as a minimum.

- Output signal: 4  20 mA DC / two-wire linear HART.

- Power supply: 24 VDC  10% by means of a passive or active intrinsically safe barrier (see T.S. TC-1/561).

- Shielded against radio interference.

- Diaphragm operating principle with variable capacitive cell.

- Microprocessor with "SMART" functions suitable for portable local calibration equipment with features listed in point 4.10.

- Total response time: not exceeding 0.5 s.

- Damping: adjustable from 0 to 60 s.

- Possibility of calibrating the zero and SPAN of the instrument:

  - local calibration with direct access to the calibration system via keys located on the instrument without jeopardising the safety of the system;

  - digital portable calibration system suitable for use in both hazardous and non-hazardous locations, connectable at all points of the current loop. Digital communication between the transmitter and the portable calibration system should display instrument functionality, main characteristics and process data, without interrupting the 4  20 mA DC variable.

- Local measurement indication: via LCD display.

- Electrical connection: ISO M20 x 1.5.

- Actual full scale (SPAN) to be chosen, when ordering, based on the operating pressure value using the possible scale ranges (RANGE( shown in the following table:

| REFERENCE | RANGE (bar) | SPAN (bar) | USE |
| --- | --- | --- | --- |
| A | 0 to 0.012 from 0 to 0.72 | 0.05 | LP |
| B | 0 to 0.06 from 0 to 0.36 | 0.1 | MPA |
| C | 0 to 0.31 from 0 to 1.86 | 0.5 | MPA |
| D | 0 to 1.1 from 0 to 6.6 | 6 | PM MPB |
| E | 0 to 3.4 from 0 to 20 | 16 | PM OP |
| F | 0 to 11 from 0 to 66 | 30 | PM OP |
| G | 0 to 35 from 0 to 200 | 80 | OP |
| H | from 0.2068428 to 1.034214 | 3 15 psi | PNEUMATIC SYSTEMS |

### Application

The electronic relative pressure transmitter can be used for the following applications:

- Standard remote control transmitter (OP-UP-PU);

- for flow rate and volume measurements, but not for gas metering systems.

## "SMART" electronic temperature transmitter - TT

The "SMART" electronic temperature transmitter must be an electrical device suitable for installation in "hazardous locations" (in relation to explosive gas atmospheres), in accordance with CEI EN 60079-10-1 and must belong to Group IIC intended for use in places with explosive atmospheres due to the presence of gas other than mines with possible presence of firedamp, have a temperature class T4 (min.), have a protection mode (or level) "ia" according to CEI EN 60079-0 and CEI EN 60079-11.

The electronic temperature transmitter must be provided with an EU type-test certificate in accordance with Directive 2014/34/EU in which the input parameters of the transmitter are specified in order to enable the system designer to produce the intrinsically safe system description document in accordance with CEI EN 60079-14 and CEI EN 60079-25.

### Mechanical characteristics

The electronic temperature transmitter must have the following mechanical characteristics:

- Process fluid measured: natural gas.

- Sensor element: platinum thermoresistance with nominal value 100 Ohm at 0°C (Pt 100) with α = 0.00385.

- Tolerance class (Pt 100): Class A according to CEI EN 60751.

- Transmitter reference accuracy: sum of digital accuracy and transmitter D/A accuracy:

  - input accuracy to the transmitter (Digital Accuracy): ±0.1°C or better;

  - output accuracy to the transmitter (D/A accuracy): ±0.02% of calibration SPAN or better.

- Suitable for direct assembly on gas pipe and complete with stainless steel thermowell made from bar with threaded "gas" connections UNI EN 10226 ND ¾" Male - ½" NPT-F.

- Protected against mechanical vibrations.

- Suitable for outdoor installation (≥ IP 65).

### Electrical characteristics

The electronic temperature transmitter must have the following electrical characteristics:

- Suitable for operation in an environment with temperatures between -20 °C and +75 °C, as a minimum.

- Output signal: 4  20 mA DC / two-wire linear HART.

- Power supply: 24 VDC  10% by means of a passive or active intrinsically safe barrier (see T.S. TC-1/561).

- Shielded against radio interference.

- Microprocessor with "SMART" functions suitable for portable local calibration equipment with features listed in point 4.10.

- Total response time: not exceeding 0.5 s.

- Damping: adjustable from 0 to 60 s.

- Possibility of calibrating the zero and SPAN of the instrument:

  - local calibration with direct access to the calibration system via keys located on the instrument without jeopardising the safety of the system;

  - digital portable calibration system suitable for use in both hazardous and non-hazardous locations, connectable at all points of the current loop. Digital communication between the transmitter and the portable calibration system should display instrument functionality, main characteristics and process data, without interrupting the 4  20 mA DC variable.

- Local measurement indication: via LCD display.

- Electrical connection: ISO M20 x 1.5.

- Intended for use in gas metering systems with venturimetric or volumetric measurement with computer according to T.S. TC-1/682.

- Measuring range: -20°C  +60°C.

### Application

The electronic temperature transmitter can be used for the following applications:

- unified transmitter for gas metering plants (TT);

- unified transmitter for remote controls (TM).

## Thermoresistance Pt 100 – RTD

The Pt 100 resistance thermometer is a simple device according to CEI EN 60079-11 (section 5.7, point a) and as such is exempt from the EU type-Examination certification requirement under Directive 2014/34/EU. The thermoresistance Pt 100 powered means of a passive intrinsically safe barrier (see T.S. TC-1/561) must have passed the applied voltage test of 500 V, in accordance with the dielectric strength requirement of CEI EN 60079-11, as defined in CEI EN 60079-25 (paragraph 11). In the absence of an EU type Examination certificate in accordance with Directive 2014/34/EU, Italgas Reti reserves the right to request the input parameters of the Pt 100 thermoresistance (Ui, Ii, Pi) in order to allow the system designer to produce the descriptive document of the intrinsically safe system in accordance with CEI EN 60079-14 and CEI EN 60079-25.

Italgas Reti is entitled to request a Pt 100 thermoresistance with an EU type Examination certificate pursuant to Directive 2014/34/EU at the time of purchase.

The Pt 100 thermoresistance must be supplied in an enclosure so as to ensure that the electrical device is suitable for installation in "hazardous locations" (in relation to explosive gas atmospheres), in accordance with CEI EN 60079-10-1, both of the IIC Group intended for use in places with explosive atmospheres due to the presence of gas other than mines with possible presence of firedamp, must have a temperature class T4 (min.), have a protection mode (or level) "d" (explosion-proof enclosure) according to CEI EN 60079-0 and CEI EN 60079-1.

### Mechanical characteristics

The Pt 100 thermoresistance must have the following mechanical properties:

- Process fluid measured: natural gas.

- Sensor element: platinum thermoresistance with nominal value 100 Ohm at 0°C (Pt 100) with α = 0.00385.

- Tolerance class (Pt 100): Class A according to CEI EN 60751.

- Suitable for direct assembly on gas pipe and complete with stainless steel thermowell made from bar with threaded "gas" connections UNI EN 10226 ND ¾" Male – ½" NPT-F.

- Suitable for outdoor installation (≥ IP 65).

### Electrical characteristics

The Pt 100 thermoresistance must have the following electrical characteristics:

- Suitable for operation in an environment with temperatures between -20 °C and +75 °C, as a minimum.

- Electrical circuit: "3-wire" or "4-wire".

- Power supply: by means of a passive or active intrinsically safe barrier (see T.S. TC-1/561).

- Electrical connection: ½" NPT-F fitted with ½" NPT-M – ½" ISO 7/1 or ISO M20 adapter.

- Intended for use in gas metering systems with venturimetric or volumetric measurement with computer according to T.S. TC-1/682.

- Measuring range: -20°C  +60°C.

### Application

The Pt 100 thermoresistance can be used for the following applications:

- unified transducer for gas metering plants (TT);

- not recommended for remote controls because it has no local indicator.

## Electro-Pneumatic Transducer - TEP

The electro-pneumatic transducer receives an electrical input signal of 4 ÷ 20 mA DC and transmits a proportional, field-adjustable pneumatic output pressure to a final control device. The pneumatic output range is 3 to 15 psig.

The operating range of the transducer input signal and output pressure must be indicated on the data plate on the enclosure.

The "SMART" electro-pneumatic transducer must be an electrical device suitable for installation in "hazardous locations" (in relation to explosive gas atmospheres), in accordance with CEI EN 60079-10-1 and must belong to Group IIC intended for use in places with explosive atmospheres due to the presence of gas other than mines with possible presence of firedamp, have a temperature class T4 (min.), have a protection mode (or level) "ia" according to CEI EN 60079-0 and CEI EN 60079-11.

The electro-pneumatic transducer must be provided with an EU type-Examination certificate in accordance with Directive 2014/34/EU in which the input parameters of the transmitter are specified in order to enable the system designer to produce the intrinsically safe system description document in accordance with CEI EN 60079-14 and CEI EN 60079-25.

### Mechanical characteristics

The electro-pneumatic transducer must have the following mechanical characteristics:

- Process fluid: natural gas with a maximum flow rate not exceeding 2 Nm3/h at a pressure of 20 psi.

- Reference accuracy (including hysteresis, linearity and dead band): ±0.5% of full scale of output SPAN or better.

- Output signal: 3 ÷ 15 psig.

- Independent linearity: ±0.5% of full scale of the output calibration range or better.

- Hysteresis: ±0.4% of full scale of the output calibration range or better.

- Supply pressure: not exceeding 50 psig.

- Maximum flow rate under steady state conditions: not exceeding 0.3 Nm3/h.

- Maximum output air capacity: not exceeding 8.0 Nm3/h at a supply pressure of 20 psig.

- Connections to supply and output pressure: ¼" NPT-F.

- Connection for venting: ¼" NPT-F.

- Threaded connections according to ASME B.1.20.1.

- Calibration of zero, calibrated range and nozzle can be performed by means of sealable adjustment screws.

- Direct or inverse action can be selected.

- Equipped with stainless steel mounting bracket for installation on 2" post.

- Suitable for outdoor installation (≥ IP 65).

### Electrical characteristics

The electro-pneumatic transducer must have the following electrical characteristics:

- Suitable for operation in an environment with temperatures between -20 °C and +60 °C, as a minimum.

- Input signal: 4  20 mA DC

- Power supply: by means of a passive or active intrinsically safe barrier (see T.S. TC-1/561).

- Shielded against radio interference.

- Electrical connection: ½" NPT-F fitted with ½" NPT-M - ISO M20 x 1.5 adapter.

### Application

The electro-pneumatic transducer can be used for the following applications:

- remote control systems (control of pressure-limiting valves and flow-rate limiting valves);

- local automatisms.

## Portable local calibration equipment for "SMART" type transmitters

The portable local calibration equipment for "SMART’” type transmitters must be an electrical device suitable for operating in "hazardous locations" (in relation to explosive gas atmospheres), in accordance with CEI EN 60079-10-1 and must belong to Group IIC intended for use in places with explosive atmospheres due to the presence of gas other than mines with possible presence of firedamp, have a temperature class T4 (min.), have a protection mode (or level) "ia" according to CEI EN 60079-0 and CEI EN 60079-11.

The portable local calibration equipment must be provided with an EU type-Examination certificate in accordance with Directive 2014/34/EU specifying the input and output parameters of the electronic equipment.

### Mechanical characteristics

The portable local calibration equipment must have the following mechanical characteristics:

- Robust, ergonomic, easily portable and lightweight.

- Easy to use and "self-protected" against overvoltage and overcurrent.

- Equipped/powered by long-life rechargeable battery.

- Equipped with a power supply/charger with coloured lights indicating battery fully charged, battery charging, no battery charging possible, etc.

- Protected against overload condition in case the power supply/charger remains connected even after charging is completed.

- Equipped with alphanumeric keyboard, function keys, navigation keys, indicator lights, etc.

- Possibility of insertion in the field by simply connecting in parallel at any point on the line traversed by the 4  20 mA DC signal without interrupting normal operation and without jeopardising the overall safety of the system, complying with the suitable insertion conditions indicated in the device manual.

- Protected against mechanical vibrations.

- Suitable for outdoor operation (≥ IP65).

### Electrical characteristics

The portable local calibration equipment, by means of LCD display and "function keys" with predetermined software (with microprocessor and built-in memories), must be able to perform the following operations/configurations:

- Calibrate the instrument throughout the desired scale range (0 to full scale) within the specific range of each instrument.

- Verify the exact analogue output of the instrument based on the signal emitted by the internal sensor.

- Change the full scale (SPAN) and related measuring units according to changed conditions of use (e.g. from 0 to 6000 mmH2O can be configured from 0 to 500 mbar).

- Define whether the output has a "direct" or "inverse" function to the input signal.

- Determine whether the output signal should be linear or quadratic.

- Determine whether the output is to be analogue 0/4  20 mA DC or digital (in serial code).

- Set minimum-maximum measuring range start/end limits.

- Define the type of signal in the event of partial failure of the transmitter in order to enable reception (Diagnostics).

- Set or vary a "time constant" for vibration damping or pendulum compensation.

- Check the ambient temperature.

- Define an identification code (instrument serial number).

- Turn the transducer into a "sample instrument" and "4  20 mA DC signal generator" to control all data processing functions downstream of the transducer (System verification).

- Other functions to be specified and detailed by the Supplier.

In addition, the portable local calibration equipment must have the following additional electrical characteristics:

- High precision.

- Suitable for operation in an environment with temperatures between 0°C and +50 °C, and 0  95% humidity.

- Shielded against radio interference.

- Low response time.

### Application

The portable "local interface'" equipment must be suitable for the local calibration of "SMART" type transmitters in intrinsically safe execution and for the measurement and transmission of pressure, flow, temperature, volume.

## Technical assessment

In relation to Legislative Decree no. 81/08, as amended and supplemented, Italgas Reti reserves the right, in its evaluation of the use of the proposed products, to consider the operational consequences deriving from the conditions of use of the equipment as prescribed by the Supplier in the "Use and Maintenance Manual".

# Marking

The products covered by this T.S. must be provided with the markings required by the EU Directives and by the relevant applicable technical standards, considering that the affixing of the CE marking, together with any other markings that may be used, is subject to the provisions of Decision no. 768/2008/EC of 9 July 2008 on a common framework for the marketing of products, implemented by the legislative decrees transposing the applicable product directives, a non-exhaustive list of which is given under "Reference standards" in this T.S.

They must therefore bear the conformity marking , affixed in the manner provided for by the legal provisions in force, together with any other markings provided for by the same directives (e.g. "specific marking of explosion protection”  in accordance with the ATEX Directive, etc.).

# TYPE TEST

In the design phase of the product, the "Type Tests" required by the Reference Standards and/or the Supplier's design standards and by the standards referred to therein, for verifying the intended end use of the product, must have been performed.

# DOCUMENTATION REQUIRED FROM THE SUPPLIER

## Supplier

- The potential Supplier must be qualified as an Italgas Supplier.

## Documents to be submitted

The potential Supplier must submit the following documentation to the PROMA-CMMAT Department at the tender stage:

- “Declaration of Conformity” with this technical specification and any specific documents mentioned in it (legislative provisions, applied standards, etc.) to which the Supplier refers for the design and construction of the product, in accordance with the requirements of UNI CEI EN ISO/IEC 17050-1 (see the example in APPENDIX 1 to this technical specification).

- Whatever else the potential Supplier considers useful to better qualify the proposed product.

## Test Documentation

The Supplier must issue a “type 3.1” Inspection Certificate in accordance with UNI EN 10204, which states that the products provided are compliant with the requirements of these specifications and which provides the test results.

Registration of the full production/test documentation completed by the Supplier must be kept (on the basis of legal provisions) for 10 years under its responsibility, and must be made available whenever requested by the Client.

## Supply Documentation

When supplying the electronic measuring instruments, transducers and local calibration equipment, the Supplier is required to provide the following documentation:

- a statement certifying ownership to market the product;

- "EU Declaration of Conformity" in accordance with legislative decrees implementing the Directives applicable to the product (e.g. ATEX, EMC, PED Directives etc.).

- EU Type Examination Certificate (Directive 2014/34/EU);

- copy of the "User Manual and Operating Instructions" (in Italian) for the correct use of the product;

- certificate of calibration and alignment in the required measuring range;

- documents compliant with Legislative Decree no. 286 of 21 November 2005, as amended.

- any other technical documents and/or drawings requested by the relevant Italgas Reti departments.

# TESTS AND INSPECTIONS

Italgas Reti reserves the right:

- To be present with its own Inspectors and/or Inspection Companies appointed by the same to carry out tests/checks at the production plant and at the Supplier's care and expense, to check the constructive and functional compliance of the materials in accordance with the specifications and/or reference standards;

- to verify, upon receipt and/or under actual conditions of use, the perfect compliance of the goods with the functional technical characteristics expressly indicated in the Contract.

It remains understood that the favourable outcome of the Inspection and checking of the materials shall not release the Supplier in any way from its responsibilities and obligations arising from every individual Contract.

## Right of the Client

In order to verify the conformity of the proposed products with the contents of this technical specification and the cited standards to which reference is made, it is Italgas Reti's right, for each purchase order, to request from the Supplier:

- the production of further relevant technical and/or graphic documentation with the indicated characteristics;

- the performance of any additional laboratory and/or field tests in relation to the required product characteristics.

# CONDITIONS OF SUPPLY

Supplier's Standard in compliance with Legislative Decree no. 152 of 3 April 2006 as amended and supplemented.

# REFERENCE STANDARDS

- Legislative Decree no. 86 of 19 May 2016 - "Implementation of Directive 2014/35/EU on the harmonisation of the laws of Member States relating to the making available on the market of electrical equipment designed for use within certain voltage limits";

- Legislative Decree no. 85 of 19 May 2016 – "Implementation of Directive 2014/34/EU on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres";

- Legislative Decree no. 194 of 06 November 2007, as amended. - "Implementation of Directive 2004/108/EC on electromagnetic compatibility, and Directive 2014/30/EU of 26 February 2014 on the harmonisation of the laws of the Member States relating to electromagnetic compatibility (recast) providing for its repeal";

- Legislative Decree no. 93 of 25 February 2000, as amended. - "Implementation of Directive 97/23/EC on pressure equipment and Directive 2014/68/EU on the harmonisation of the laws of the Member States relating to the making available on the market of pressure equipment (recast), providing for its repeal";

- Legislative Decree no. 49 of 14 March 2014, as amended. – "Implementation of Directive 2012/19/EU on Waste from Electrical and Electronic Equipment (WEEE)';

- Italian Legislative Decree no. 27 of 04 March 2014, as amended – "Implementation of Directive 2011/65/EU on the restriction of the use of certain hazardous substances in electrical and electronic equipment";

- Law no. 186 of 1 March 1968 - "Provisions concerning the production of materials, equipment, machinery, electrical and electronic installations and systems";

- Legislative Decree no. 81 of 09 April 2008, as amended. - “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”;

- Legislative Decree no. 152 of 03 April 2006, as amended. - “Environmental standards”;

- Legislative Decree no. 286 of 21 November 2005, as amended. - “Provisions for the regulatory reorganisation of the regulated liberalisation of the road haulage business”;

- CEI EN 60079-0 (CEI 31-70) - “Explosive atmospheres - Part 0: Equipment - General Requirements";

- CEI EN 60079-1 (CEI 31-58) “Explosive atmospheres - Part 1: Equipment protected by explosion-proof enclosures “d”;

- CEI EN 60079-11 (CEI 31-78) “Explosive atmospheres - Part 11: Equipment with intrinsically safe protection mode "i"";

- CEI EN 60079-25 (CEI 31-79) “Explosive atmospheres - Part 25: Intrinsically safe electrical systems";

- CEI EN 60079-10-1 (CEI 31-87) “Explosive atmospheres - Part 10-1: Classification of areas - Explosive gas atmospheres";

- CEI EN 60079-14 (CEI 31-33) “Explosive atmospheres - Part 14: Design, selection and installation of electrical systems";

- CEI EN 60751 (CEI 65-8) – "Industrial platinum resistance thermometers and platinum temperature sensors";

- CEI EN 60529 (CEI 70-1) – "Degrees of protection provided by enclosures (IP Code)";

- CEI EN 60770-1 (CEI 65-4) – "Transmitters used in industrial process control systems - Part 1: Methods for performance evaluation";

- CEI EN 60770-3 (CEI 65-103) – "Transmitters used in industrial process control systems - Part 3: Performance Evaluation Methods for Smart Transmitters";

- UNI EN 10204 - “Metallic products - Types of inspection documents”;

- UNI CEI EN ISO/IEC 17050-1 - "Conformity assessment - Supplier's declaration of conformity. Part 1: General requirements”;

- ISO 965 – "ISO general purpose metric screw threads";

- ASME PTC 19.3 TW – "Thermowells Performance Test Codes";

- ASME B1.20.1 –“Pipe Threads, General Purpose (Inch)”.

# APPENDICES

- APPENDIX 1 -	“Sample declaration of conformity with this technical specification”

## APPENDIX 1

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN lSO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(4)	S.T.V.F.C. TC-1/631	"Electronic measuring instruments, transducers and           Edition 1 of 15/06/2017

local calibration equipment

Additional information:

(5) 	...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(6) 	............................................................. 			......................................................................................................................

(Name and position) 						(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- List all the products for which approval for company use is requested (name, type, model), stating any codes assigned by the Supplier itself and, where existing, the relevant material codes assigned by Italgas.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

Supplier means the party responsible for the design and construction of the products or its legal representative.

If the differential pressure transmitter is not requested mounted on a manifold integrated with the instrument during the purchase phase, then it is the responsibility of the Supplier to specify the process connections of the instrument and the manifold (instrument side) and ensure the compatibility of the process connection of the instrument to the manifold.

Linear or square root output must be specified during the purchasing phase.

To be added to the total response time of the sensor.

If the differential pressure transmitter is not requested mounted on a manifold integrated with the instrument during the purchase phase, then it is the responsibility of the Supplier to specify the process connections of the instrument and the manifold (instrument side) and ensure the compatibility of the process connection of the instrument to the manifold.

Linear or square root output must be specified during the purchasing phase.

To be added to the total response time of the sensor.

If the absolute pressure transmitter is not requested mounted on a manifold integrated with the instrument during the purchase phase, then it is the responsibility of the Supplier to specify the process connections of the instrument and the manifold (instrument side) and ensure the compatibility of the process connection of the instrument to the manifold.

To be added to the total response time of the sensor.

If the absolute pressure transmitter is not requested mounted on a manifold integrated with the instrument during the purchase phase, then it is the responsibility of the Supplier to specify the process connections of the instrument and the manifold (instrument side) and ensure the compatibility of the process connection of the instrument to the manifold.

To be added to the total response time of the sensor.

If the relative pressure transmitter is not requested mounted on a manifold integrated with the instrument during the purchase phase, then it is the responsibility of the Supplier to specify the process connections of the instrument and the manifold (instrument side) and ensure the compatibility of the process connection of the instrument to the manifold.

To be added to the total response time of the sensor.

If the relative pressure transmitter is not requested mounted on a manifold integrated with the instrument during the purchase phase, then it is the responsibility of the Supplier to specify the process connections of the instrument and the manifold (instrument side) and ensure the compatibility of the process connection of the instrument to the manifold.

To be added to the total response time of the sensor.

The reference accuracy of the transmitter does not take Pt 100 into account.

This accuracy is relative to the D/A conversion stage.

To be added to the total response time of the sensor.

The parameters Ci and Li are negligible.

The Supplier must indicate the recommended supply pressure.

Venting must be remote, as the continuous operating discharge of the pneumatic relay must be piped to the outside.