- “TECHNICAL SPECIFICATION FOR SUPPLY ASSESSMENT AND INSPECTION”

- S.T.V.F.C. 2401301

- TURBINE AND ROTARY PISTON METERS FOR METHANE GAS

| Compiled by | INGE-NOTEAD-NORTEC Federico FENU | FENU |
| --- | --- | --- |
| Checked by | NORTEC Enrico VARESE | VARESE |
| Checked by | MISURA SVILMIS Sergio GHIA | GHIA |
| Checked by | PROCU/BENI Silvio FASSINO | FASSINO |
| Checked by | HSEQ Carlo SALAMONE | SALAMONE |
| Checked by | ASSQUAL Massimo Mazzari | MAZZARI |
| Approved by | NOTEAD Sandro LACIDOGNA | LACIDOGNA |
| Approved by | MISURA Eduardo PASTORE | PASTORE |

- SUMMARY

1.	PRELIMINARY INFORMATION	3

1.1.	Cancels and replaces	3

1.2.	Reason for issue	3

1.3.	List of changes to this specification	3

1.4.	Company departments mentioned in the document	3

2. 	PURPOSE AND FIELD OF APPLICATION	3

2.1.	Purpose	3

2.2.	Field of application	4

3. 	SPECIFICATIONS	4

3.1.	Technical assessment	4

4. 	COMPANY APPROVAL	4

4.1.	Characteristicsand reference standards	4

4.2.	Pressure testing	5

4.3.	Implementation methods	6

5.	Characteristics of the meters approved and supplied	8

5.2.	Marking	8

5.2.1.	Barcode	8

5.2.2.	Two-dimentional code	10

5.3. 	Pressure and Temperature Intakes	11

5.4	Totaliser	11

5.5	Operating and Maintenance Instructions	11

5.6.	Traceability	11

5.7.	Compliance check	11

5.8.	Random checks periodic checks	12

6.	PRODUCT WARRANTY	13

7.	CONDITIONS OF SUPPLY	14

7.1.	Packaging.	14

7.2.	 Shipping	14

8.	DOCUMENTATION FOR THE APPROVAL FOR COMPANY USE PROCESS	15

9. 	REFERENCE STANDARDS	16

10.	APPENDICES	18

# 1.	PRELIMINARY INFORMATION

## 1.1.	Cancels and replaces

"Technical Specification for Gas Meter Evaluation " T.S. 24013041 edition 6 of 30 November 2010.

## 1.2.	Reason for issue

Updating the S.T.V. 24013041, Edition 6 of 30.11.2010, became necessary so as to adapt it to the current legislation and company choices.

## 1.3.	List of changes to this specification

- Addition of the Meter Supply and Testing section.

- Adaptation of document to legislative requirements.

- Addition of turbine meter table for pressures 4 < P max ≤ 12 bar.

- Addition of turbine meter table for pressures 12 < P max ≤ 24 bar.

- Deletion of G 1000 classes for rotary piston meters and G 40 turbine meters since no longer produced.

- Supply request added for bolts for flange assembly. Two of these must have a hole suitable for sealing the meters.

## 1.4.	Company departments mentioned in the document

- INGE-NOTEAD-NORTEC – Technical Regulatory Engineering and Documentary Assessment

- PROCU – GOODS – Goods Procurement

- MISURA - SVILMIS –  Measurement Development

- MISURA – LAB – Measurement Laboratory

- ASSQUAL – Quality Assurance

- HSEQ - Health, Safety, Environment, Quality

# 2. 	PURPOSE AND FIELD OF APPLICATION

## 2.1.	Purpose

This Specification applies to turbine and rotary piston gas meters and defines:

- the characteristics of the material and reference standards;

- the types of checks and test methods used to obtain authorization for company use;

## 2.2.	Field of application

It applies whenever material covered by this specification must be authorised for company use, produced by a new potential Supplier or by an existing one.

# 3. 	SPECIFICATIONS

- This Specification must be understood as an integral part of the "ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF THE ITALGAS GROUP."

- The fluid that the meters covered by this specification must measure is natural gas, suitably odourised, with the characteristics set out in the Ministerial Decree of 19 February 2007, published in the Official Gazette no. 65 of 19 March 2007.

## 3.1.	Technical assessment

Italgas reserves the right, in the overall assessment of the products proposed, to also consider the operational maintenance instructions for the devices as described in the relative instructions.

# 4. 	COMPANY APPROVAL

- This specification defines the technical requirements of Italgas.

- The drawings shown in the various appendices should be considered as a "standard model shown as an example", except for the specified dimensions and technical characteristics, which should be considered as binding.

The material characteristics, production, control and certification must meet the reference standards stated in paragraph 8.

## 4.1.	Characteristics and reference standards

According to the tests envisaged by standards UNI EN 12261 and UNI EN 12480, the meters must not have errors that exceed the maximum permissible errors listed in Table 1.

Table 1 Permissible measurement errors.

| - FLOW RATE - m3/h | - Maximum Permissible Error on New Meters | - Maximum Permissible Error FOR DURATION TESTS |
| --- | --- | --- |
| - Qmin  Q < Qt | - 2.0% | - 2.6% |
| - Qt  Q  Q max | - 1.0% | - 1.3% |

Q = Flow rate

Q min = Minimum flow rate defined in UNI EN 12261 and UNI EN 12480

Q max = Maximum flow rate defined in UNI EN 12261 and UNI EN 12480

Q t = Transition flow rate defined in UNI EN 12261 and UNI EN 12480

The Manufacturer must declare the maximum pressure drop at Qmax

## 4.2.	Pressure testing

All turbine meters to be used at pressures > 4 bar must have passed the metrological pressure test in accordance with UNI EN 12261. The meter must show, on the data plate, the value of the pressure range at which it can be used.

The material characteristics, production, control and certification must meet the reference standards stated in paragraph 8.

For meters with operating pressures ≤ 4 bar:

- meter body made of spheroidal cast iron, steel or aluminium;

- flow rate range Qmin/Qmax of 1:20 and 1:50;

- fitted with self-lubricating support;

- body connections and mechanical strength ANSI 150.

For meters with operating pressures 4 < Pmax ≤ 12 bar:

- meter body made of spheroidal cast iron or steel;

- flow rate range Qmin/Qmax of 1:20 and 1:50;

- fitted with self-lubricating support;

- body connections and mechanical strength ANSI 150.

For meters with operating pressures 12 < Pmax ≤ 24 bar:

- meter body made of spheroidal cast iron or steel;

- flow rate range Qmin/Qmax of 1:20 and 1:50;

- fitted with self-lubricating support;

- body connections and mechanical strength ANSI 300.

For turbine meters with operating pressures Pmax > 50 ≤ 100 bar:

- meter body made of steel;

- flow rate range Qmin/Qmax of 1:20 and 1:50;

- fitted with self-lubricating support with oil pump;

- body connections and mechanical strength ANSI 600.

Turbine meters must have a built-in flow rectifier.

Rotary piston and turbine meters must be fitted with pulse emitters with the following characteristics, in accordance with the standards referred to:

- external connector, protection class IP65 (ISO 60529), predisposed for application of a seal;

- intrinsically safe operation (CEI EN 50014 and CEI EN 50020 standards);

- for the high-frequency pulse generator, the generated power signal must comply with UNI EN 12480 (for rotating piston meters), and UNI EN 12261 (for turbine meters).

- low-frequency (LF) and high-frequency (HF) pulse emitter, at Italgas’ request, as indicated in the table in Appendix 1 (Rotary pistons).

- low-frequency (LF) , and high-frequency (HF) pulse emitter, at Italgas’ request, as indicated in the table in Appendices 2 and 3 (Turbine).

## 4.3.	Implementation methods

For the performance of tests for company approval, Italgas will select and take directly from the Supplier's warehouse the following number of meters to subject to testing:

Table 2 Sampling for company approval

| Caliber | Quantity |
| --- | --- |
| G25 (*) | 2 |
| G40 (*) | 2 |
| G65 | 3 |
| G100 | 3 |
| G160 | 3 |
| G250 | 2 |
| G400 | 2 |
| G650 | 2 |
| G1000 | 1 |

(*) For rotary piston meters only

The meters must be fitted with a pulse emitter.

The checks carried out on the meters will be as follows:

- measurement error on new meters; tests will be carried out at the flow rates in Table 1, repeated 3 times;

Table 3  Test flow rates

| Type | Flow rate range | Q min | 0.02 Q max | 0.05 Q max | 0.1 Q max | 0.15 Q max | 0.25 Qmax | 0.4 Qmax | 0.7 Qmax | Qmax |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rotary pistons | 1:20 | X |  | X | X |  | X | X | X | X |
| Rotary pistons | 1:50 | X |  | X |  | X | X | X | X | X |
| Turbine | 1:20 | X |  | X | X |  | X | X | X | X |
| Turbine | 1:50 | X | X | X |  | X | X | X | X | X |

- pressure absorption: the values measured must not be greater than the values declared by the manufacturer and those indicated in Appendices 1, 2 and 3;

- 1,000 hour duration test as foreseen by the standards with verification of the measurement error and pressure absorption when new and after 1,000 hours (see point 5.1 and point 8.2 UNI EN 12480; point 5.2.4 UNI EN 12261).

This test must be performed by the Supplier, and carried out by a laboratory registered on the EA circuit, which is compliant with the requirements of UNI CEI EN ISO/IEC 17025.

All meters tested must meet the requirements set out in Table 1, both when new and after duration tests, and the requirements of point 8 UNI EN 12480 and point 5.2.4 UNI EN 12261.

- Metrological repeatability

- For rotary piston meters (see point 5.4 UNI EN 12480).

- For turbine meters (see point 5.2.2 UNI EN 12261).

In addition, during the metrological performance check, a congruity check is carried out between the numerical totaliser and the pulses transmitted by it, having an appropriate number (approx. 1000) of pulses transmitted: no discrepancies between the totaliser and the pulses measured, gross of the tolerance concerning the weight of the pulse (1 imp = x m3), are allowed.

After evaluating the results provided by the Supplier of tests carried out by Laboratories belonging to the EA circuit and in accordance with the requirements of UNI CEI EN ISO/IEC 17025, Italgas may grant provisional approval during the performance of company approval tests.

The provisional approval, which is in any case conditional to the evaluation of the first results of the tests, allows the Supplier to supply the meters and must be made definitive or revoked at the end of the company approval tests.

Following a request for approval for company use of meters with CE-MID marking already approved for company use with EEC stamp pursuant to Presidential Decree no. 857 of 23/08/1982, Italgas may grant approval for company use for similar MID-marked models also, subject to evaluation of the results provided by the Supplier of tests carried out by Laboratories belonging to the EA circuit and compliant with the requirements of UNI CEI EN ISO/IEC 17025.

# Characteristics of the meters approved and supplied

  - Amendments

After obtaining approval for company use, the Supplier must not make any significant changes to the approved products without prior notification to Italgas, which reserves the right to accept or reject the changes made, and request possible laboratory tests.

By way of example, significant changes are considered to be those concerning:

- measurement system;

- clock box;

- pulse connectors;

- construction dimensions.

## 5.2.	Marking

It must comply with the requirements of UNI EN 12261 and UNI EN 12480.

The supply of meters with a marking or stamping date referring to the year preceding the year of supply is not permitted, with the sole exception of supplies at the beginning of the year.

## 5.2.1.	Barcode

The meters must be provided with a suitable bar code, on which the following data must appear sequentially:

-	meter plate									(8 characters)

-	meter type code (assigned by U.C.Metric) 				(4 characters)

-	meter brand code (assigned by U.C.Metric) 				(3 characters)

- year of production								(2 characters)

- date of marking (YY/MM)						(4 characters)

-	number of indicator cogwheels (m3 only) 				(1 character)

-	construction details (see Appendix 4) 					(2 characters)

- repair company code (put zeros “00”)					(2 characters)

- year of re-marking/repair (put zeros “00”)				(2 characters)

- repair/re-marking information (put zeros “00”)			(1 character)

- various information (put zeros “00”)					(2 characters)

N.B. The serial numbers to be affixed to the meters are assigned by Italgas, to each supplier, in a specific letter of communication.

Printed characters must be strictly 31 to allow readability.

In addition, the following requirements must be observed:

- dimensions of the removable adhesive label (23 x 88 mm) or (25 x 110 mm).

- code 2/5 interleaved low/medium density from 0.38 mm to 0.25 mm

- height of the bars no less than 11 mm and in any case adequate for the length of the code.

The bars must be black on a white base.

- The upper part of the label must show in sequence, without spaces, the year of construction, the manufacturer's brand name, the plate number (e.g. YYYYBBBPPPP), for a total of 15 characters (transcription in plain text).

- The total 31 characters must be written in the lower part.

- The information contained in the barcode must be readable using a DATALOGIC barcode wand, model P31R - 132A at medium resolution.

## 5.2.2.	Two-dimentional code

In addition to the bar code (point 4.2.1), a "two-dimensional code" with the following characteristics must be provided:

- two-dimensional Quick Response code (QR Code)”

- the size of the QR code for a string of 31 numeric characters.

E.g.: “1234567809012345678901234567890” must be:

- PIXELS: 135 x 135

- Cm: 3.58 x 3.58

As shown in the example below

135 Pixels/3.58 cm

cm

135 Pixels/3.58 cm

This code must contain the same information as the bar code (point 4.2.1), in the same, identical sequence.

The unencrypted numerical sequence of the two-dimensional code may be printed outside the QR code, as shown in the example below.

860000073090271010035230000000

The code must be placed, in an irremovable manner on the package containing the meter.

## 5.3. 	Pressure and Temperature Intakes

These must be made in accordance with the requirements of Standard UNI/TS 11291.

The meter must be set up to allow connection to pressure and temperature transmitters; it must have intakes as indicated below:

Pressure:

- ¼" male GAS threaded connection

Temperature:

thermowell (1 or 2) suitable for housing a sensor, with male threaded connection ND ¾", with cap, of the following dimensions:

- diameter 6 mm;

- length 65 mm.

## 5.4	Totaliser

In addition to complying with the standards and laws in force, the totaliser must be constructed in such a way as to render the internal clock mechanisms invisible, with the exception of the front, displaying consumption and data plate.

The totaliser and its drive must be sealed, or capable of being sealed, in such a way as to prevent unauthorised intervention without breaking the seal. Any eyelet systems (screws, bolts, etc.) must have holes with a minimum diameter of 2 mm to allow the passage of a sealing cable.

## 5.5	Operating and Maintenance Instructions

Each meter, or group of meters, must be supplied with installation, operation and maintenance manuals, as required by the relevant standards.

The manuals must be in Italian.

## 5.6.	Traceability

The traceability of both the meter serial number and all the most significant components of the meter: body, clock, etc. must be ensured.

In addition, the following documentation, in computerised form (EXCEL), must be provided to MISURA - GESTMIS (Italgas Largo Regio Parco 9 - 10153 Turin) for each meter, aggregated by production batch:

- error curve (performed at Qmin - 0.25 Qmax - Qmax);

- pair of pre-calibration error correction wheels (constant), with indication of the correction value (if any).

Documentation must be provided on a monthly basis and refer to the production delivered in the month. The results of the statistical monthly check must also be provided.

## 5.7.	Compliance check

The compliance of supplies is assessed on the basis of:

- verifications and calibrations requested of the Supplier from its own laboratory or carried out by a laboratory belonging to the EA circuit, compliant with the requirements of UNI CEI EN ISO/IEC 17025, to the extent of one sample as per Table 4 with reference to the test lot.

The tests will be carried out at the flow rates shown in Table 3, repeated 3 times; conformity will be assessed on the basis of tests on new meters only and the meters tested must meet the requirements set out in Table 1.

The Supplier must issue certification in accordance with UNI EN 10304 3.1 for the lot submitted for testing.

These checks, in agreement with the Supplier, can also be carried out in the Italgas laboratory.

Table 4 Meter sampling

| Caliber | Quantity |
| --- | --- |
| G25 (*) | 1 |
| G40 (*) | 1 |
| G65 | 2 |
| G100 | 2 |
| G160 | 2 |
| G250 | 1 |
| G400 | 1 |
| G650 | 1 |
| G1000 | 1 |

(*) For rotary piston meters only

c) sporadic checks carried out by Italgas on new meters,

d) random checks and periodic checks (see point 5.8).

Individual meters that do not meet the requirements set out in Tables 1 and 2 during the checks referred to in point b) will be considered "individually non-compliant" and replaced under warranty by the Supplier.

Individual meters that during the checks referred to in point c) do not meet the requirements set out in point 5.8 below, will be considered "individually non-compliant" and replaced under warranty by the Supplier.

If the “individually non-compliant" meters exceed 5% of the meters tested each year, for each size and type, the Supplier is notified and the supply is temporarily suspended with the issue of a Non-Conformity Report and request for a corrective action plan.

Once the technical corrective solution has been identified, it must be verified on a representative sample, equal to twice the sample number in Table 5.

All the meters of the representative sample envisaged must meet the requirements set out in Table 1.

Only if this verification is successful can supply be resumed.

## Random checks periodic checks

In the case of periodic and random checks subject to legislative provisions, the MPE values for defining the conformity of meters will be those defined in the aforementioned legislative provisions.

Meters found to be non-compliant during periodic and random checks, including meter checks requested by end customers, shall be replaced under warranty by the Supplier.

# PRODUCT WARRANTY

The metrological performance, mechanical and construction characteristics of the instrument must be guaranteed for 5 years under normal use.

The following must be replaced under warranty:

- all meters found to be non-compliant as a result of supply checking activities (see point 5.7),

- all meters that for any reason are subject to verification (see point 5.8).

# 7.	CONDITIONS OF SUPPLY

- Turbine and rotary piston meters must be supplied with the respective gaskets required, while counter flanges must be made available to the Italgas Warehouse.

- All meters must be supplied with the appropriate bolts necessary for assembling the flanges. Two of these (one per flange), must also have suitable 2 mm holes to allow the passage of the sealing cable as shown in the figure below.

## 7.1.	Packaging.

The meters must be individually packaged respecting the standard dimensions of 80 x 120 cm and a maximum height of 140 cm. The Europallet, in turn, must be packed and reinforced on its four corners to prevent any movement of the load contained therein.

The barcode of the individual meters, possibly in sequence from… to… must be applied to each individual  package and to the Europallet.

## 7.2.	 Shipping

Shipping shall be to the address specified on each line of the purchase order, with delivery carriage paid and unloaded on the ground by the Supplier.

# 8.	DOCUMENTATION FOR THE APPROVAL FOR COMPANY USE PROCESS

- The potential Supplier must:

- be certified in accordance with UNI EN ISO 9000;

- be qualified as a SNAM supplier.

- Statement certifying ownership to market the product;

- The potential Supplier must provide the Italgas PROCU - GOODS Department with the following information:

- declaration of conformity with this specification, as required by UNI CEI EN ISO/IEC 17050-1 (see example in Appendix 7);

For all turbine meters to be used at pressures > 4 bar, documentation must be provided on the performance of the metrological pressure test in accordance with the requirements of UNI EN 12261. The meter must show, on the data plate, the value of the pressure range at which it can be used.

Italgas, reserves the right to require the supplier:

- to produce further technical documentation and/or drawings;

- to carry out any laboratory and/or field tests to check the conformity of the proposed products with the content of this Appendix and the standards it refers to.

- Any other technical documents and/or drawings requested by the relevant Italgas departments,

- “Operating Instructions” for the correct use of the product;

- "Certificate of conformity", issued by a recognised certification body, to Legislative Decree no. 93 of 25 February 2000 (PED Directive).

- If, on the basis of the design of a project intended for use under pressure (PED Directive), the Supplier determines that its product does not have the characteristics defined by the aforementioned directive, it must in any case submit a declaration of inclusion within art. 3 paragraph 3 of the aforementioned directive to certify the exemption of the product in compliance with the provisions of the same paragraph;

- a FAC-SIMILE of the marking on the product, or on the accompanying documents, bearing the data required by Presidential Decree 126 of 23 March 1998 (where applicable), Legislative Decree no. 93 of 25 February 2000 and by the technical standards applied.

On the basis of the product provided a declaration of conformity must be submitted, referring to:

- Declaration of Conformity with Supplement no. 64 to the Official Gazette 17-3-2007 Legislative Decree no. 22 of 2 February 2007. Implementation of Directive 2004/22/EC on measuring instruments (MID).

- Declaration of Conformity pursuant to Presidential Decree no. 857 of 23/08/1982 (specify references more precisely).

- "EC Declaration of Conformity" in accordance with Presidential Decree no. 126 of 23 March 1998 (ATEX 1 Directive).

- If, on the basis of the design of a product intended for use in potentially explosive atmospheres (ATEX 1 Directive), the Supplier determines that its product does not fall within the requirements of the aforementioned directive, the Supplier must submit a declaration of assumption of responsibility which certifies that, following the risk analysis carried out, the product does not have any potential ignition sources of its own, and therefore does not fall within the scope of Presidential Decree no. 126/98 (ATEX 1 Directive) and can therefore be installed in all the zone types referred to in Legislative Decree no. 233/03 ( ATEX 2 Directive).

# 9. 	REFERENCE STANDARDS

- Italian Metric Law (from Royal Decree 7088 of 23 August 1890 onwards);

- Law no. 186 of 1 March 1968 - "Provisions concerning the production of materials, equipment, machinery, electrical and electronic installations and systems";

- Law no. 791 of 18 October 1977 - "Implementation of the Directive of the Council of the European Communities (no. 72/23/EEC) on the safety guarantees that electrical equipment designed for use within certain voltage limits must possess";

- Law no. 1083 of 6 December 1971 - “Standards for the safe use of fuel gas”;

- Legislative Decree no. 93 of 25 February 2000 "Implementation of Directive 97/23/EC PED on pressure equipment";

- Presidential Decree 23 March 1998 no. 126 - "Regulations containing standards for the implementation of Directive 94/9/EC concerning equipment and protective systems intended for use in potentially explosive atmospheres" (ATEX 1);

- DIRECTIVE 2014/32/EU OF THE EUROPEAN PARLIAMENT AND OF THE COUNCIL

- of 26 February 2014 on the harmonisation of the laws of the Member States relating to making available on the market of measuring instruments (recast)

- UNI EN 682 "Elastomeric seals. Requisites of elastomeric materials used in pipes and fittings carrying gas and hydrocarbon fluids";

- UNI EN 12261 "Turbine gas meters";

- UNI EN 12480 "Rotary piston gas meters";

- UNI EN ISO 9001 “Quality management systems  - Requirements”;

- UNI CEI EN ISO/IEC 17050-1 - "Conformity assessment - Supplier's declaration of conformity - Part 1: General requirements”;

- Ministerial Decree 16 April 2008: “Technical regulations for the design, construction, testing, operation and supervision of works and distribution systems and direct lines for natural gas with a density not exceeding 0.8”;

- Ministerial Decree 17 April 2008: “Technical regulations for the design, construction, testing, operation and supervision of works and plants for the distribution of natural gas with a density not exceeding 0.8”;

- Italian Legislative Decree no. 81 of 9 April 2008 “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”, as amended;

- Italian Legislative Decree no. 106 of 3 August 2009 “Integration and correction of Legislative Decree of 9 April 2008 on the protection of health and safety in the workplace”;

- Presidential Decree no. 246 of 21 April 1993 - "Regulation implementing Directive 89/106/EEC on construction products";

- Legislative Decree no. 194 of 6 November 2007 - "Implementation of Directive 2004/108/CE on the approximation of the laws of Member States relating to electromagnetic compatibility and repealing Directive 89/336/EEC”;

- Legislative Decree no. 233 of 12 June 2003 – "Implementation of Directive 1999/92/EC on minimum requirements for improving the safety and health protection of workers exposed to the risk of explosive atmospheres";

- UNI 9034 - “Gas distribution pipelines with maximum operating pressure (MOP) not exceeding 0.5 MPa (5 bar) - Materials and jointing systems”;

- UNI EN ISO 286-1 - "Geometrical product specifications (GPS) - ISO code system for tolerances on linear sizes - Part 1: Fundamental principles for tolerances, deviations and fits”.

- UNI EN ISO 286-2 - "Geometrical product specifications (GPS) - ISO code system for tolerances on linear sizes - Part 2: Tables of standardised tolerance classes and limit deviations of holes and shafts".

- UNI EN ISO 22768-1 - "General tolerances. Tolerances for linear and angular dimensions without individual tolerance indications".

- UNI EN 22768-2 - Geometric tolerances for features without individual tolerance indications".

- UNI EN 228-1 "Pipe threads where pressure-tight joints are not made on the thread" - Designation, dimensions and tolerances"

- UNI EN 1706 "Aluminium and aluminium alloys – Castings – Chemical composition and mechanical properties";

- UNI EN 10087 "Free-cutting steels – Technical delivery conditions for semi-finished products, hot-rolled bars and rods";

- UNI EN 10130 "Cold rolled low carbon steel flat products for cold forming – Technical delivery conditions";

- UNI EN 10152 "Electrolytically zinc-coated cold-rolled, steel flat products for cold forming – Technical delivery conditions";

- UNI EN 10346 "Continuously hot dip coated steel flat products for cold forming – Technical delivery conditions";

- UNI EN 10216-1 "Seamless steel tubes for pressure purposes - Technical delivery conditions - Part 1: Non-alloy steel tubes for use at room temperature";

- UNI EN 10297 "Seamless circular steel tubes for mechanical and general engineering purposes – Technical delivery conditions";

- Supplement no. 64 to the Official Gazette 17-3-2007 Legislative Decree no. 22 of 2 February 2007 "Implementation of Directive 2004/22/EC on measuring instruments (MID)";

- LAW no. 99 of 23 July 2009 (Official Gazette no. 176 of 31-7-2009 - Ordinary Supplement no. 136) "Provisions for the development and internationalisation of enterprises, as well as on energy2.

- UNI/TS 11291-1: "Gas metering systems - Hourly-based gas metering systems - Part 1: General characteristics for remote reading or remote management system";

- UNI/TS 11291-2: "Gas metering systems - Hourly-based gas metering systems - Part 2: CTE Protocol";

- UNI/TS 11291-3: "Gas metering systems - Hourly-based gas metering systems - Part 3: CTR Protocol";

- UNI/TS 11291-4: "Gas metering systems - Hourly-based gas metering systems. Requirements for measuring units > G 40 or 65 m3/h";

- UNI/TS 11291-5: "Gas metering systems - Hourly-based gas metering systems. Requirements for measuring units between 16 m3/h and 65 m3/h (meter ≥ G10 and ≤ G40)";

- UNI/TS 11291-8: "Gas metering systems - Hourly-based gas metering systems - Part 8: Protocols for the remote operation of metering units for the distribution network".

# 10.	APPENDICES

Appendix 1:	Rotary piston meters P max ≤ 5 bar

Appendix 2:	Turbine meters P max ≤ 4 bar

Appendix 3:	Turbine meters 4 < P max ≤ 12 bar

Appendix 4:		Turbine meters 12 < P max ≤ 24 bar

Appendix 5	High pressure turbine meters 50 ≤ P max ≤ 100 bar (ANSI 600)

Appendix 6:	Construction specifications codified by Italgas

Appendix 7:		Sample declaration of conformity with this technical specification

Appendix 8:		Sample declaration of exclusion from Directive ATEX 2

Appendix 9:		Sample declaration of SOUND ENGINEERING PRACTICE (SEP)

APPENDIX 1

ROTARY PISTON METERS

P max ≤ 5 bar

| Caliber | Material code | Minimum flow rate m3/h | Maximum flow rate m3/h | No. Indicating Totaliser Wheels m3 | Diameter Flanged Connections ANSI 150 mm | Face-to-face and centre-to-face L mm | No. of pulse intakes at low frequency (lf) | LF pulses m3/pulse  1 hz at qmax | p max mbar (1) | Installation (2) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| G25 | 2401581 | 2 | 40 | 6 | 50 | 171 | 1 | 0.1 | 0.5 | H + V |
| G25 | 2401781 | 0.8 | 40 | 6 | 50 | 171 | 1 | 0.1 | 0.5 | H + V |
| G40 | 2401591 | 3.2 | 65 | 6 | 50 | 171 | 1 | 0.1 | 1.0 | H + V |
| G40 | 2401791 | 1.3 | 65 | 6 | 50 | 171 | 1 | 0.1 | 1.0 | H + V |
| G65 | 2401601 | 5 | 100 | 6 | 50 | 171 | 1 | 0.1 | 2.3 | H + V |
| G65 | 2401801 | 2 | 100 | 6 | 50 | 171 | 1 | 0.1 | 2.3 | H + V |
| G100 | 2401611 | 8 | 160 | 7 | 80 | 171 | 1 | 1 | 2.5 | H + V |
| G100 | 2401811 | 3.2 | 160 | 7 | 80 | 171 | 1 | 1 | 2.5 | H + V |
| G160 | 2401621 | 13 | 250 | 7 | 80 | 241 | 1 | 1 | 3.0 | H + V |
| G160 | 2401821 | 5 | 250 | 7 | 80 | 241 | 1 | 1 | 3.0 | H + V |
| G250 | 2401631 | 20 | 400 | 7 | 100 | 241 | 1 | 1 | 4.0 | H + V |
| G250 | 2401831 | 8 | 400 | 7 | 100 | 241 | 1 | 1 | 4.0 | H + V |
| G400 | 2401641 | 32 | 650 | 7 | 150 | 450 | 1 | 1 | 5.0 | H + V |
| G400 | 2401841 | 13 | 650 | 7 | 150 | 450 | 1 | 1 | 5.0 | H + V |
| G650 | 2401651 | 50 | 1000 | 7 | 150 | 500 | 1 | 1 | 5.0 | H |
| G650 | 2401851 | 20 | 1000 | 7 | 150 | 500 | 1 | 1 | 5.0 | H |

NOTES:

(1) P = Pressure drop with natural gas at Qmax, density 0.83 kg/m3

(2)  H= horizontal, V= vertical

Protective coating: complies with EN 12480 point 6.2.2.

APPENDIX 2

TURBINE METER

P max ≤ 4 bar

| Caliber | Material Code | Minimum Flow rate m3/h | Maximum Flow rate m3/h | No. Indicating Totaliser Wheels m3 | Diameter Flanged Connections ANSI 150 mm | Face-to-face and centre-to-face L mm | No. of Pulse Intakes at Low Frequency (LF) | No. of Pulse Intakes at High Frequency (HF) | LF pulses m3/pulse 1 Hz at Qmax | P Max mbar (1) | Installation (2) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| G65 | 2401902 | 5 | 100 | 6 | 50 | 150 | 2 | 1 | 0.1 | 15 | H + V |
| G65 | 2402101 | 2 | 100 | 6 | 50 | 150 | 2 | 1 | 0.1 | 15 | H + V |
| G100 | 2401912 | 8 | 160 | 7 | 80 | 240 | 2 | 1 | 1 | 15 | H + V |
| G100 | 2402111 | 3.2 | 160 | 7 | 80 | 240 | 2 | 1 | 1 | 15 | H + V |
| G160 | 2401922 | 13 | 250 | 7 | 80 | 240 | 2 | 1 | 1 | 15 | H + V |
| G160 | 2402121 | 5 | 250 | 7 | 80 | 240 | 2 | 1 | 1 | 15 | H + V |
| G250 | 2401932 | 20 | 400 | 7 | 100 | 300 | 2 | 1 | 1 | 15 | H + V |
| G250 | 2402131 | 8 | 400 | 7 | 100 | 300 | 2 | 1 | 1 | 15 | H + V |
| G400 | 2401941 | 32 | 650 | 7 | 150 | 450 | 1 | 1 | 1 | 15 | H + V |
| G400 | 2402141 | 13 | 650 | 7 | 150 | 450 | 1 | 1 | 1 | 15 | H + V |
| G650 | 2401951 | 50 | 1000 | 7 | 150 | 450 | 1 | 1 | 1 | 15 | H + V |
| G650 | 2402151 | 20 | 1000 | 7 | 150 | 450 | 1 | 1 | 1 | 15 | H + V |
| G1000 | 2401961 | 80 | 1600 | 8 | 200 | 600 | 1 | 1 | 10 | 15 | H + V(*) |
| G1000 | 2402161 | 32 | 1600 | 8 | 200 | 600 | 1 | 1 | 10 | 15 | H + V(*) |
| G1600 | 2401971 | 130 | 2500 | 8 | 250 | 750 | 1 | 1 | 10 | 15 | H + V(*) |
| G1600 | 2402171 | 50 | 2500 | 8 | 250 | 750 | 1 | 1 | 10 | 15 | H + V(*) |
| G2500 | 2401981 | 200 | 4000 | 8 | 300 | 900 | 1 | 1 | 10 | 15 | H + V(*) |
| G2500 | 2402181 | 80 | 4000 | 8 | 300 | 900 | 1 | 1 | 10 | 15 | H + V(*) |
| G4000 | 2401991 | 320 | 6500 | 8 | 400 | 1200 | 1 | 1 | 10 | 15 | H + V(*) |
| G4000 | 2402191 | 130 | 6500 | 8 | 400 | 1200 | 1 | 1 | 10 | 15 | H + V(*) |

NOTES:

(1) P = Pressure drop with natural gas at Qmax, density 0.83 kg/m3

(2)  H= horizontal, V= vertical

V (*) = Vertical installation may be requested as required.

Protective coating: complies with EN 12261 point 6.3.3.

APPENDIX 3

TURBINE METER

4 < P max ≤ 12 bar

| Caliber | Material Code | Minimum Flow rate m3/h | Maximum Flow rate m3/h | No. Indicating Totaliser Wheels m3 | Diameter Flanged Connections ANSI 150 mm | Face-to-face and centre-to-face L mm | No. of Pulse Intakes at Low Frequency (LF) | No. of Pulse Intakes at High Frequency (HF) | LF pulses m3/pulse 1 Hz at Qmax | P Max mbar (1) | Installation (2) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| G65 | 2401908 | 5 | 100 | 6 | 50 | 150 | 2 | 1 | 0.1 | 15 | H + V |
| G100 | 2401918 | 8 | 160 | 7 | 80 | 240 | 2 | 1 | 1 | 15 | H + V |
| G160 | 2401928 | 13 | 250 | 7 | 80 | 240 | 2 | 1 | 1 | 15 | H + V |
| G250 | 2401938 | 20 | 400 | 7 | 100 | 300 | 2 | 1 | 1 | 15 | H + V |
| G400 | 2401948 | 32 | 650 | 7 | 150 | 450 | 1 | 1 | 1 | 15 | H + V |
| G650 | 2401953 | 50 | 1000 | 7 | 150 | 450 | 1 | 1 | 1 | 15 | H + V |
| G1000 | 2401968 | 80 | 1600 | 8 | 200 | 600 | 1 | 1 | 10 | 15 | H + V(*) |
| G1600 | 2401978 | 130 | 2500 | 8 | 250 | 750 | 1 | 1 | 10 | 15 | H + V(*) |
| G2500 | 2401988 | 200 | 4000 | 8 | 300 | 900 | 1 | 1 | 10 | 15 | H + V(*) |
| G4000 | 2401998 | 320 | 6500 | 8 | 400 | 1200 | 1 | 1 | 10 | 15 | H + V(*) |

NOTES:

(1) P = Pressure drop with natural gas at Qmax, density 0.83 kg/m3

(2)  H= horizontal, V= vertical

V (*) = Vertical installation may be requested as required.

Protective coating: complies with EN 12261 point 6.3.3.

APPENDIX 4

TURBINE METER

12 < P max ≤ 24 bar

| Caliber | Material Code | Minimum Flow rate m3/h | Maximum Flow rate m3/h | No. Indicating Totaliser Wheels m3 | Diameter Flanged Connections ANSI 300 mm | Face-to-face and centre-to-face L mm | No. of Pulse Intakes at Low Frequency (LF) | No. of Pulse Intakes at High Frequency (HF) | LF pulses m3/pulse 1 Hz at Qmax | P Max mbar (1) | Installation (2) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| G65 | 2402108 | 5 | 100 | 6 | 50 | 150 | 2 | 1 | 0.1 | 15 | H + V |
| G100 | 2402118 | 8 | 160 | 7 | 80 | 240 | 2 | 1 | 1 | 15 | H + V |
| G160 | 2402128 | 13 | 250 | 7 | 80 | 240 | 2 | 1 | 1 | 15 | H + V |
| G250 | 2402138 | 20 | 400 | 7 | 100 | 300 | 2 | 1 | 1 | 15 | H + V |
| G400 | 2402148 | 32 | 650 | 7 | 150 | 450 | 1 | 1 | 1 | 15 | H + V |
| G650 | 2402153 | 50 | 1000 | 7 | 150 | 450 | 1 | 1 | 1 | 15 | H + V |
| G1000 | 2402168 | 80 | 1600 | 8 | 200 | 600 | 1 | 1 | 10 | 15 | H + V(*) |
| G1600 | 2402178 | 130 | 2500 | 8 | 250 | 750 | 1 | 1 | 10 | 15 | H + V(*) |
| G2500 | 2402188 | 200 | 4000 | 8 | 300 | 900 | 1 | 1 | 10 | 15 | H + V(*) |
| G4000 | 2402198 | 320 | 6500 | 8 | 400 | 1200 | 1 | 1 | 10 | 15 | H + V(*) |

NOTES:

(1) P = Pressure drop with natural gas at Qmax, density 0.83 kg/m3

(2)  H= horizontal, V= vertical

V (*) = Vertical installation may be requested as required.

Protective coating: complies with EN 12261 point 6.3.3.

APPENDIX 5

ANSI 600 HIGH PRESSURE TURBINE METERS

up to 100 bar

| Caliber | Material code | Minimum flow rate m3/h | Maximum flow rate m3/h | No. Indicating Totaliser Wheels m3 | Diameter Flanged Connections ANSI 600 mm | Face-to-face and centre-to-face L mm | No. of pulse intakes at low frequency (LF) | No. of pulse intakes at High Frequency (HF) | LF pulses m3/pulse 1 Hz at Qmax | P max mbar (1) | Installation (2) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| G65 | 2401934 | 5 | 100 | 6 | 50 | 150 | 2 | 1 | 0.1 | 15 | H + V(*) |
| G65 | 2402134 | 2 | 100 | 6 | 50 | 150 | 2 | 1 | 0.1 | 15 | H + V(*) |
| G100 | 2401935 | 8 | 160 | 7 | 80 | 240 | 2 | 1 | 1 | 15 | H + V(*) |
| G100 | 2402135 | 3 | 160 | 7 | 80 | 240 | 2 | 1 | 1 | 15 | H + V(*) |
| G160 | 2401936 | 13 | 250 | 7 | 80 | 240 | 2 | 1 | 1 | 15 | H + V(*) |
| G160 | 2402136 | 5 | 250 | 7 | 80 | 240 | 2 | 1 | 1 | 15 | H + V(*) |
| G250 | 2401937 | 20 | 400 | 7 | 100 | 300 | 2 | 1 | 1 | 15 | H + V(*) |
| G250 | 2402137 | 8 | 400 | 7 | 100 | 300 | 2 | 1 | 1 | 15 | H + V(*) |

NOTES:

(1) 	P = Pressure drop with natural gas at Qmax, density 0.83 kg/m3

(2) 	H= horizontal

V (*) = Vertical installation may be requested as required.

Protective coating: complies with EN 12261 point 6.3.3.

APPENDIX 6

Construction specifications codified by Italgas

| Code | DESCRIPTION |
| --- | --- |
| 00 | NO SPECIAL FEATURES |
| 10 | ELECTRONIC TOTALIZER |
| 11 | LF PULSE EMITTER |
| 12 | ENCODER |
| 13 | LF + HF PULSE EMITTER |

APPENDIX 7

SAMPLE DECLARATION OF CONFORMITY

(1)	Logo and name of Supplier

Address

(2)	 prot. xyz

Product:	Product description (e.g. gas turbine meter).

The following products manufactured by us (3):

| Our material code (4) | Italgas material code (5) |
| --- | --- |
| xxx | 2401971 |
| xxx | yyy |
| xxx | yyy |

comply with the following reference ITALGAS documents (6):

for example:

- S.T.V. 0000300 “TECHNICAL PROVISIONS OF GENERAL CHARACTERISTICS FOR MATERIAL TABLES AND TECHNICAL NOTES” ed. 0 of 23.07.2003

- N° T. 150/0/00/GG "THREADED SOCKET LINES FOR CONNECTIONS FROM CAST IRON PIPES B.P AND MPA "dated 05 December 2000

(7) They also comply with the provisions of current legislation.

Place, date

Name and Surname

Role of the representative of the company

Signature

1	On letterhead paper or if visible on applied stamps.

2	If possible, indicate a unique identifying code to trace the document.

3	List all the products for which company use authorisation is being requested.

4	For each individual product supplied, state the material code used by the Supplier.

5	For each individual product supplied, please quote the Italgas’ material code (e.g. 2401935), which can be found in the Italgas reference documents. If there are none, please contact the SERCOP Department to assign them.

6	Attention!!! Include the reference documents for the proposed products.

7	Any additional information may be included at the Supplier's discretion as stated in UNI CEI EN ISO/IEC 17050-1.

APPENDIX 8

ATEX EXCLUSION DECLARATION

We ......................................................................................................................

(name of organisation)

with registered office in .............................................................................................................

(address)

as the ……………….…………………………….…………………………………..……………

(Manufacturer / Authorised Representative)

declare under our sole responsibility that the products series

………………………………………………………..….………………………………….…………..

………………………………………………………..….………………………………….…………..

(name, type or model, batch, group or serial numbers)

described in the Technical Specification / document(s)

………………………………………………………...….………………………………….…………..

…………………………………………………………………………………………….…………...…

(when necessary)

to which this declaration refers, comply with the following legislative / regulatory document(s)

…………………………………………………………………………………………….…………...…

…………………………………………………………………………………………….…………...…

(title(s) and/or number(s) and date(s) of publication of the standard(s) or other legislative and/or regulatory document(s))

and, according to Article 1, subsection 3a) of Directive 94/9/EC of 23 March 1994 (Presidential Decree no. 126 of 23 March 1998) and Chapter 4 of ATEX GUIDELINES (third edition), based on an ATEX analysis (see subsection 4.1 of the aforementioned ATEX GUIDELINES), do not fall within the scope of the Directive 94/9/EC, as they do not risk causing an explosion due to the lack of potential ignition sources, as defined in Standard UNI EN 1127-1, when used in systems that comply with the following legislative and/or regulatory documents

…………………………………………………………………………………………….…………...…

…………………………………………………………………………………………….…………...…

(title and/or number and date of publication of legislative and/or regulatory documents)

They can therefore be installed in all types of zones as defined in Legislative Decree no. 81 of 9 April 2008,  Title XI, as amended.

| …………………………………………. | ……………………………………………………………. |
| --- | --- |
| (place and date of issue) | (name and signature or equivalent stamp of authorised person) |

APPENDIX 9

CONFORMITY FORM

DECLARATION OF FALLING WITHIN THE SCOPE OF ARTICLE 3, SUBSECTION 3 OF THE LEGISLATIVE DECREE NO. 93

(SEP Declaration)

We ......................................................................................................................

(name of organisation)

with registered office in .............................................................................................................

(address)

as the ……………….…………………………….…………………………………..……………

(Manufacturer / Authorised Representative)

we declare that, following the analysis carried out in accordance with Legislative Decree no. 93 of 25 February 2000 (PED directive), the series products:

…………………..………..……………………………………………………………………………….

…………………..………..……………………………………………………………………………….

(name, type or model, batch, group or serial number)

described in the document:

…………………..………..……………………………………………………………………………….

…………………..………..……………………………………………………………………………….

(title and/or number and date of publication of the Standard(s) or other regulatory document(s))

to which this declaration refers, fall under Article 3, subsection 3 of Legislative Decree no. 93 of 25 February 2000, and are therefore subject to the provisions thereof. Consequently, the products mentioned are not subject to CE marking for the application of Legislative Decree no. 93 of 25 February 2000.

SOUND ENGINEERING PRACTICE