“TECHNICAL SPECIFICATION FOR EVALUATION, SUPPLY AND TESTING”

S.T.V.F.C. 2401300

Diaphragm meters for methane gas and LPG

| Compiled by | SERTEC-NORM | TARANTINO, ANDREA |
| --- | --- | --- |
| Checked by | SERTEC-NORM | VARESE, ENRICO |
| Checked by | PROMA/CMMAT | FASSINO, SILVIO |
| Checked by | PROMA-MATMA | SCOTTO, ENRICO |
| Checked by | SERTEC-LAB | SALATI, EUGENIO |
| Checked by | MISURA-SVILMIS | GHIA, SERGIO |
| Checked by | HSEQ | BOLZONI, GIANLUCA |
| Approved by | SERTEC | COMAZZI, MARCO |

SUMMARY

1	PRELIMINARY INFORMATION	4

1.1	Cancels and replaces	4

1.2	Reason for issue	4

1.3	Company departments mentioned in the document	4

1.4	Definitions	4

2	PURPOSE AND FIELD OF APPLICATION	4

2.1	Purpose	4

2.2	Field of application	4

3	SPECIFICATIONS	4

4	Technical characteristics	5

4.1	Dimensions	6

4.2	Metrological characteristics	6

4.3	Pressure and Temperature Intakes for meters size ≥ G 10	7

4.4	Totaliser	7

4.5	Seals	7

4.6	Attachment spigots	8

4.7	Traceability	8

4.8	Technical assessment	8

5	Markings	8

5.1	Barcode	8

5.2	Two-dimentional code	9

6	COMPANY APPROVAL	11

6.1	Implementation of company approval tests	11

6.1.1	Testing under normal environmental operating conditions	11

6.1.2	Consistency check between numerical totaliser and pulses transmitted by the same	11

6.2	Test results	11

6.3	Amendments	11

7	Supply compliance check	12

7.1	General Information	12

7.2	Supply compliance check	12

7.2.1	Meter testing at the Supplier’s premises	12

7.2.2	Testing at Italgas Reti laboratories	14

7.3	Random and periodic checks for all sizes	16

8	PRODUCT WARRANTY	16

9	DOCUMENTATION required from the Supplier	17

9.1	Supplier	17

9.2	Documentation for the company approval process	17

9.3	Supply Documentation	17

10	REFERENCE STANDARDS	18

11	APPENDICES	19

12	Annex	19

APPENDIX 1	20

APPENDIX 2	21

APPENDIX 3	22

APPENDIX 4	23

APPENDIX 5	24

APPENDIX 6	25

APPENDIX 7	26

APPENDIX 8	27

APPENDIX 9	28

APPENDIX 10	29

APPENDIX 11	30

APPENDIX 12	31

# PRELIMINARY INFORMATION

## Cancels and replaces

This specification cancels and replaces S.T.V. 2401300, edition 7 of 30.11.2010 as amended and supplemented.

## Reason for issue

Updating the S.T.V. 2401300 and its reissue in the form of Technical Specifications, became necessary as a result of:

- new legislative context;

- issuing of new national and European standards (e.g. UNI, CEI, EN, etc.)

- addition of Table 2 for pressure drops of meters.

## Company departments mentioned in the document

- SERTEC-NORM = Standard

- PROMA-CMMAT = Materials

- MISURA-SVILMIS = Measurement Development

- MISURA-SUSCON = Meter Replacement Assistance

- SERTEC-LAB = Laboratory

- PROMA-MATMA = Material Management

## Definitions

The technical definitions contained in this specification conform to those of the standards listed in “Reference standards”.

# PURPOSE AND FIELD OF APPLICATION

## Purpose

This T.S. applies to diaphragm meters for methane gas and LPG with a maximum operating pressure of 0.5 bar.

It defines:

- the main characteristics of the material and reference standards;

- the types of checks methods used to obtain authorization for company use;

- the checks of supply conformity (inspection/testing).

## Field of application

This Technical Specification applies whenever material covered by this specification must be approved for company use, produced by a new potential Supplier or by an existing one and supply conformity needs to be checked.

# SPECIFICATIONS

- This technical specification must be understood as an integral part of the "ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS."

- This specification contains the minimum technical requirements demanded by Italgas Reti based on the reference Legislative and Technical Standards.

- It is the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. sharp edges, incorrect directions for use and maintenance, etc.), which may jeopardise the health and safety of the Client's workers in relation to the provisions of Legislative Decree no. 81/08, as amended and supplemented.

- For any technical and operational aspects that conflict with or are not mentioned in this technical specification but that nevertheless pertain to the design, installation, maintenance and use of the products themselves, it is the Supplier's responsibility to refer to the regulations in force.

- The fluid that the products covered by this T.S. must measure is natural gas, suitably odourised, with the characteristics set out in the Ministerial Decree of 19 February 2007, published in the Official Gazette no. 65 of 19.03.2007, and, in some cases, LPG.

# Technical characteristics

The diaphragm meters covered by this Technical Specification, are subject to Law no. 186/68, relating to the realisation and construction of materials, equipment, machinery, installations and electrical and electronic systems “to standard”; they must therefore be suitable for their intended use and ensure, as regards the materials used and their construction, adequate resistance to the environmental and mechanical factors to which they may be exposed during operation.

The diaphragm meters considered in this T.S. refer to the following product standard:

- UNI EN 1359 - "Diaphragm gas meters".

The material characteristics, production, control and certification must meet the reference standards stated in Chapter 10.

They are also subject to a whole series of legislative provisions, in relation to the required characteristics, materials and intended use, including:

- Italian Legislative Decree no. 22 of 2 February 2007 as amended relating to the implementation of Directive 2004/22/EC on measuring equipment and Directive 2014/32/EU of 26 February 2014 as amended by the Delegate Directive (EU) 2015/13 of 31 October 2014 on the harmonisation of the laws of the Member States relating to the making available on the market of measuring equipment (recast), providing for its repeal;

- Italian Legislative Decree 85 of 19 May 2016 – "Implementation of Directive 2014/34/EU on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres".

- Law no. 99 of 23 July 2009, as amended, on provisions for the development and internationalisation of enterprises, as well as on energy.

- Ministerial Decree no. 93 of 21 April 2017, as amended – "Regulation concerning the criteria for performing subsequent metrological checks on gas meters and volume conversion devices, pursuant to Legislative Decree no. 84 of 19 May 2016 "Implementation of Directive 2014/32/EU" on measuring instruments (MID);

- Italian Legislative Decree no. 152 of 3 April 2006, as amended and supplemented, on environmental regulations;

- Italian Legislative Decree no. 81 of 9 April 2008, as amended on the Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace.

Lastly, they must comply with the provisions of AEEGSI Resolution ARG/GAS 631/13 and the technical standards referred to therein, a non-exhaustive list of which is provided in Chapter 10 of this T.S.

Unless explicitly referred to otherwise, the standards cited are those related to the latest edition, including any variants/updates and/or corrigenda published.

## Dimensions

The dimensions of the meters are shown in the respective figures in Appendices 1 to 9 for each individual size covered by this T.S.

The drawings shown in the various appendices, however, should be considered as a "standard model shown as an example", except for the specified dimensions and technical characteristics, which should be considered as binding.

## Metrological characteristics

In accordance with the respective product standards, the meters must not produce errors exceeding the maximum tolerable errors stated in table 1 and 2.

Table 1 Permissible measurement errors for meters with CE-MID marking for class 1.5 (Standard UNI EN 1359)

| FLOW RATE m3 / h | INITIAL MAXIMUM PERMISSIBLE ERROR | SUBSEQUENT MAXIMUM PERMISSIBLE ERROR |
| --- | --- | --- |
| Qmin ≤ Q < Qt | ± 3.0 % | ± 6.0 % |
| Qt ≤ Q ≤ Qmax | ± 1.5 % | ± 3.0 % |

N.B.

The meter must not exploit the maximum tolerable errors or systematically favour one of the parts.

Q = Flow rate

Qmin = Minimum flow rate defined by product standard

Qmax = Maximum flow rate defined by product standard

Qt= Transition flow rate defined by the manufacturer which is between the maximum and minimum flow rate, (normally Qt is 0.1 Qmax).

Table 2 Maximum permissible values for pressure drop

| Qmax (m3/h) | Initial (mbar) | After duration (mbar) |
| --- | --- | --- |
| 2.5 ≤ Qmax ≤ 16 | 2.0 | 2.2 |
| 25 ≤ Qmax ≤ 65 | 3.0 | 3.3 |
| 100 ≤ Qmax ≤160 | 4.0 | 4.4 |

## Pressure and Temperature Intakes for meters size ≥ G 10

In meters where correction to the standard conditions is obtained by means of temperature and pressure probes, pressure and temperature intakes must be made on the meter to allow inspections to be carried out in accordance with the requirements of Standard UNI/TS 11291 indicated below:

Pressure:

a pressure intake with a ND ¼" male GAS threaded connection suitable for housing a pressure sensor for measuring gas pressure.

Temperature:

two thermometer pockets with caps, suitable for housing temperature sensors of the following dimensions:

- diameter 6 mm;

- length 65 mm.

The required pressure and temperature intakes must not obstruct installation of the meter.

## Totaliser

In addition to complying with the standards and laws in force, the totaliser must be constructed in such a way as to render the internal clock mechanisms invisible, with the exception of the front, displaying consumption and data plate.

It must have at least one eyelet (minimum hole diameter 2 mm), preferably located in the upper part of the totaliser, which allows the passage of a cable for sealing.

## Seals

Two seals with a thickness of 3 mm must be provided inside the box with the meters, with characteristics as per T.S. 2945300 "Synthetic rubber seals".

## Attachment spigots

In addition to complying with the dimensional characteristics required in the "Appendices" to this document, the inlet and outlet spigots of the meters must have the minimum length specified below in order to allow for easy sealing of the meter. This minimum length must be ensured for at least the entire area where the swivel nut is located, calculated using the maximum diameter of the swivel crown plus 20 mm, irrespective of the shape of the case.

The minimum spigot length is given in Table 3 below.

Table 3 Minimum length of attachment spigots

| METER MODEL | MINIMUM LENGTH OF ATTACHMENT SPIGOTS mm |
| --- | --- |
| G 2.5 | 18 |
| G 4 | 18 |
| G 6 | 18 |
| G 10 | 18 |
| G 16 | 18 |
| G 25 | 25 |

## Traceability

The traceability of both the meter serial number and all the most significant components of the meter: case, clock, diaphragms etc. must be ensured.

## Technical assessment

Italgas Reti reserves the right, in the overall assessment of the products proposed, to also consider the operational maintenance instructions for the devices as described in the relative instructions.

# Markings

The meter must comply with the requirements of UNI EN 1359 and be approved in accordance with the requirements of Legislative Decree no. 84 of 19 May 2016.

The supply of meters with a marking date referring to the year preceding the year of supply is not permitted, except for deliveries at the beginning of the year.

## Barcode

Italgas Reti also requires meters to be supplied with an appropriate barcode which must contain the following sequential numerical data:

- meter plate (8 characters)

-	meter type code                                          				(4 characters)

-	meter brand code                                         				(3 characters)

-	year of production 									(2 characters)

-	date of marking (YY/MM) 								(4 characters)

-	number of indicator cogwheels (whole m3 only) 			(1 character)

-	construction details (see Appendix 10) 					(2 characters)

-	repair company code (put zeros “00”)					(2 characters)

-	year of re-marking/repair (put zeros “00”)				(2 characters)

-	re-stamping/repair information (put zeros “00”) 			(1 character)

-	various information (put zeros “00”)						(2 characters)

N.B. The serial numbers to be affixed to the meters are assigned by Italgas Reti to each supplier, in a specific letter of communication.

Printed characters must be strictly 31 to allow readability.

The construction details coded by Italgas Reti are shown in the Table of the APPENDIX 10.

The barcode must be labelled with black bars on a white background and the following requirements must be observed:

- dimensions of the removable adhesive label on the package (23 x 88 mm) or (25 x 110 mm);

- code 2/5 interleaved low/medium density from 0.38 mm to 0.25 mm;

- height of the bars no less than 11 mm and in any case adequate for the length of the code;

- the upper part of the label must show in sequence, without spaces, the year of construction, the manufacturer's brand name, the plate number (e.g. YYYYBBBPPPP), for a total of 15 characters (transcription in plain text);

- the total 31 characters must be written in the lower part;

- the information contained in the barcode must be readable using a DATALOGIC barcode wand, model P31R - 132A at medium resolution.

The barcode must be printed on a removable label placed on the package containing the meter.

## Two-dimentional code

In addition to the barcode (point 5.1), a “two-dimensional code” must be provided, which must contain the same information as the barcode.

The QR Code must have the same following characteristics:

- two-dimensional Quick Response code (QR Code);

- the size of the QR code for a string of 31 numeric characters.

E.g.: “1234567809012345678901234567890” must be:

- PIXELS: 135 x 135;

- cm: 3.58 x 3.58

As shown in the example below

135 Pixels/3.58 cm

cm

135 Pixels/3.58 cm

The aforesaid code must contain the same information as the bar code (point 5.1), in the same, identical sequence.

The unencrypted numerical sequence of the two-dimensional code may be printed outside the QR code, as shown in the example below.

860000073090271010035230000000

The QR Code (non-removable adhesive type) must be placed on the package containing the meter.

# COMPANY APPROVAL

## Implementation of company approval tests

Italgas Reti will choose and take samples directly from the Supplier's warehouse:

- meters up to and including G6: 12 meters sampled, of which 6 will be tested;

- meters ≥ G10: 4 meters sampled, 3 of which will be tested.

The meters must be fitted with a pulse emitter.

### Testing under normal environmental operating conditions

The checks to be carried out on the meters are:

- measurement error when new; tests will be performed with air fluid at flow rates Qmin, 3Qmin, 0.1Qmax, 0.2Qmax, 0.4Qmax, 0.7Qmax and Qmax, repeated at least 3 times;

- pressure absorption (see point 5.2 of UNI EN 1359);

### Consistency check between numerical totaliser and pulses transmitted by the same

A consistency check between the numerical totaliser and the pulses transmitted by it is envisaged.

The tests must be carried out by transmitting at least 1,000 pulses: no discrepancies are permitted between the totaliser and the pulses measured, gross of the tolerance for the weight of the pulse (1 imp = x dm3).

## Test results

After evaluating the results provided by the Supplier of tests carried out by Laboratories belonging to the EA circuit and in accordance with the requirements of UNI CEI EN ISO/IEC 17025, Italgas Reti may grant provisional approval during the performance of company approval tests.

The provisional approval, which is in any case conditional to the evaluation of the first results of the tests, allows the Supplier to supply the meters and must be made definitive or revoked at the end of the company approval tests.

Furthermore, Italgas Reti reserves the right to carry out fewer or additional tests on a sample basis with respect to the provisions of point 6.1.

Following the successful completion of all tests, the Company will issue approval for use of the meters.

## Amendments

After obtaining approval for company use, the Supplier must not make any significant changes to the approved products without prior notification to Italgas Reti, which reserves the right to accept or reject the changes made, and to require laboratory tests and technical documentation.

By way of example, significant changes are considered to be those concerning:

- measuring system (e.g. diaphragms, grille and cabinets);

- clock box;

- pulse connectors;

- building dimensions.

The Supplier undertakes to provide Italgas Reti, annually (reference month: December), with a technical data sheet listing the changes made in the interval since the date of company approval or since the last technical data sheet sent.

Furthermore, Italgas Reti reserves the right to perform confirmation tests on the product to maintain its approval for company use in accordance with the procedures set out in this Specification.

# Supply compliance check

The Supplier shall submit a "Quality Control Plan" to the SERTEC-LAB Unit for approval prior to delivery of the meters.

## General Information

The duration of meter marking is regulated by Law no. 99 of 23 July 2009, as amended and by Ministerial Decree no. 93 of 21 April 2017, as amended. These legislative documents stipulate that the temporal validity of the metric stamps and CE marking affixed to gas meters with a maximum flow rate up to 10 m³/h is 15 years, starting from the year of their affixing during verification or conformity assessment prior to being placed on the market. In particular, Ministerial Decree 93/2017, as amended, rules out the performance of periodic verifications before the expiry of 15 years, for meters with a maximum flow rate up to 10 m3/h, unlike the provisions for meters with higher flow rates for which the duration is extended to 16 years.

## Supply compliance check

.

### Meter testing at the Supplier’s premises

The request for testing must be made by the manufacturer to SERTEC/LAB and must be accompanied by the file with the "meter master data" referred to in point 8.2 below; SERTEC/LAB together with MISURA/SVILMIS assists in carrying out the testing of the meters at the manufacturer's premises. In certain cases, SERTEC/LAB may waive its right to attend the inspection, notifying the Supplier. The number of meters to be checked is determined on the basis of the quantity to be delivered and the tables in ISO Standard 3951-1 "Sampling procedures for inspection variables (Annex A)", below.

From Table A, the general inspection level I is chosen, combined with the "reduced" inspection column of the "s-method" in Table B.

In order to judge the conformity of the lot, the same requirements as in the following point 7.2.2.3 must be met.

Following a successful test result at the place of production or its abandonment, the manufacturer sends SERTEC/LAB a number of meters, as stipulated below, belonging to the lot to be tested, duly packaged,

SERTEC/LAB informs the manufacturer of the number of meters to send, determined on the basis of the quantity to be delivered and the tables in ISO Standard 3951-1 "Sampling procedures for inspection variables (Annex A)", below.

From Table A, the general inspection level I is chosen, combined with the "reduced" inspection method “sigma-σ" of Table B (highlighted).

Table A. Lot Size and General Inspection Level

| No. of meters | I | II | III |
| --- | --- | --- | --- |
| 2 to 8 | B | B | B |
| 9 to 15 | B | B | C |
| 16 to 25 | B | C | D |
| 26 to 50 | C | D | E |
| 51 to 90 | C | AND | F |
| 91 to 150 | D | F | G |
| 151 to 280 | F | G | H |
| 281 to 500 | F | H | J |
| 501 to 1,200 | G | J | K |
| 1,200 to 3,200 | H | K | L |
| 3,201 to 10,000 | J | L | M |
| 10,001 to 35,000 | K | M | N |
| 35,001 to 150,000 | L | N | P |
| 150,001 to 500,000 | M | P | Q |
| over 500,000 | N | Q | R |

Table B

|  | "s-method" |  | "σ-method" |  |
| --- | --- | --- | --- | --- |
| Sampling letter | Normal inspection | AT THE MANUFACTURER’S PREMISES Reduced inspection SERTEC-LAB MISURA-SVILMIS | Normal inspection | IN THE LABORATORY Reduced inspection SERTEC-LAB MISURA-SVILMIS |
| B | 3 | 3 | 2 | 2 |
| C | 4 | 3 | 3 | 2 |
| D | 6 | 3 | 4 | 2 |
| E | 9 | 4 | 6 | 3 |
| F | 13 | 6 | 8 | 4 |
| G | 18 | 9 | 10 | 6 |
| H | 25 | 13 | 12 | 8 |
| J | 35 | 18 | 15 | 10 |
| K | 50 | 25 | 18 | 12 |
| L | 70 | 35 | 21 | 15 |
| M | 95 | 50 | 25 | 18 |
| N | 125 | 70 | 32 | 21 |
| P | 160 | 95 | 40 | 25 |
| Q | 200 | 125 | 50 | 32 |
| R | 250 | 160 | 65 | 40 |

Concurrently, the Manufacturer sends the meters, in the specified quantity, so that they reach SERTEC/LAB within 5 working days of factory inspection. The meters are selected randomly by SERTEC/LAB, and may be the same, entirely or partially, as those verified by the Supplier. The Supplier only ships the lot after obtaining release for delivery.

The Manufacturer must issue certification in accordance with UNI EN 10204-3.1 for the lot submitted for testing.

The Manufacturer must also issue certification in accordance with UNI EN 10204-3.2 for tests attended by SERTEC/LAB.

### Testing at Italgas Reti laboratories

Upon receiving the meters sent by the Supplier, SERTEC/LAB analyses the lot, performing a calibration error check.

All verification activities are carried out within five working days of receipt.

At the end of the checks SERTEC/LAB, in the case of a positive result, releases the lot for delivery, informing the manufacturer, PROMA/MATMA and MISURA/SUSCON. In the case of a negative result, instead, the provisions of point 7.2.2.3. apply.

#### Requirements for calibration benches used by SERTEC/LAB

For the purpose of ascertaining the metrological conformity of the meter being tested as regards the maximum permissible errors, MPE, the calibration benches of the Asti Laboratory guarantee overall BMC (Best Measurement Capability) calibration uncertainties less than/equal to one third of the most restrictive MPE, as provided for by the WELMEC Guide 11.1, May 2008, European Cooperation in Legal Metrology, a document in accordance with the European MID Directive:

BMC ≤ 1/3 MPE

MPE: ±3.0 % ÷ ± 1.5 %

#### Performance of calibrations

The activities to be performed by SERTEC/LAB are as follows:

- receive the meters and schedule verification of the same;

- carry out the verification on each individual meter at the following 4 test flow rates: Qmin, 0.2Qmax, 0.4÷0.7Qmax e Qmax;

- segregate the meters found to be non-compliant, in a suitable manner, e.g. in the warehouse, affixing a label stating "NOT COMPLIANT";

- forward the results of the checks and any non-conformities found to the manufacturer, with cc to PROMA/MATMA, MISURA/SVILMIS and MISURA/SUSCON;

- make meters available for field installation as quickly as possible.

#### Conformity of individual meters following calibration checks

For a meter forming part of a supply lot to be judged compliant, the following requirements must be met:

em ≤ MPE1 for individual test flow rates

where em is the average percentage error,

MPE = 	± 3.0% at Qmin (1 test only without repetition);

± 1.5% at the other flow rates 0.2 Qmax, 0.4 ÷ 0.7 Qmax and Qmax (3 repetitions)

Note: Errors are rounded to the first decimal place. If these values are exceeded, the supply of meters is temporarily suspended. SERTEC/LAB will issue a Non-Compliance Report to the Supplier, requesting a Corrective Action Plan from the Supplier, with cc to PROMA/MATMA, MISURA/SVILMIS and MISURA/SUSCON.

Following the issue of the Non-Compliance Report and the consequent Corrective Action Plan, SERTEC/LAB and MISURA/SVILMIS agree with the Supplier on the verification of a new representative sample of the lot, with reference to inspection level I, method-s sampling, reduced inspection, of the technical standard ISO 3951-1:2005 "Sampling procedures for inspection variables".

All the meters in the new sample must comply.

Only if this verification is successful can supply be resumed, with cc to PROMA/MATMA and MISURA/SUSCON. If the result remains negative, the entire lot must be rejected, a new Corrective Action Plan will be requested to investigate the causes of the rejection, which must be evaluated and approved by SERTEC/LAB and MISURA/SVILMIS.

SERTEC/LAB will keep PROMA/MATMA and MISURA/SUSCON informed of the progress of the Non-Compliance.

## Random and periodic checks for all sizes

In the case of periodic and random checks subject to legislative provisions, the MPE values for defining the conformity of meters will be those defined in the aforementioned legislative provisions.

Meters found to be non-compliant during periodic and random checks, including meter checks requested by end customers, shall be replaced under warranty by the Supplier.

# PRODUCT WARRANTY

The metrological performance, mechanical and construction characteristics of the instrument must be guaranteed for 5 years under normal use and installed as required by UNI 9036. The warranty shall apply if the performance deviation can be attributed to a defect in the meter ex works.

# DOCUMENTATION required from the Supplier

## Supplier

The potential Supplier must be qualified as an Italgas Reti Supplier.

## Documentation for the company approval process

The potential Supplier must submit the following documentation to the SERTEC-NORM Department:

- “Declaration of conformity” with this Technical Specification and any specific documents mentioned in it (legal provisions, applied standards, MID Directive, ATEX, EMC, PED, etc.), to which the Supplier refers for the design and construction of the product, as indicated in the UNI CEI EN ISO/IEC 17050-1 standard (see the example given in APPENDIX 11 of this Technical Specification).

## Supply Documentation

Upon delivery of the meters, the Supplier must produce the following documentation:

- "EU Declaration of Conformity" pursuant to Legislative Decree no. 84 of 19 May 2016 “Implementation of the MID Directive" on measuring instruments (MID).

- "EU Declaration of Conformity" pursuant to Legislative Decree no. 85 of 19 May 2016.. If, on the basis of the design of a product intended for use in potentially explosive atmospheres, the Supplier determines that its product does not fall within the provisions of the aforementioned Directive, the Supplier must submit a declaration of assumption of responsibility which certifies that, following the risk analysis carried out, the product does not have any potential ignition sources of its own, and therefore does not fall within the scope of Legislative Decree no. 85 of 19 May 2016 – see APPENDIX 12 – and can therefore be installed in all the zone types referred to in Legislative Decree no. 233/03.

- Copy of the "Instruction Manual" (in Italian) for the correct use of the product.

- FACSIMILE of the marking on the product, or on the accompanying documents, bearing the data required by Legislative Decree no. 85 of 19 May 2016, (where applicable), Legislative Decree no. 93 of 25 February 2000, as amended, and the technical standards applied.

- Any other technical documents and/or drawings requested by the relevant Italgas Reti Departments.

- Italgas Reti, reserves the right to require the Supplier:

- to produce further technical documentation and/or drawings;

- to carry out any laboratory and/or field tests to check the conformity of the proposed products with the content of this Appendix and the standards it refers to.

# REFERENCE STANDARDS

- Italian Metric Law (from Royal Decree no. 7088 of 1890 onwards);

- Ministerial Decree of 19 February 2007 – "Approval of the technical regulation on the chemical-physical characteristics and presence of other components in combustible gas to be transported". (OG General Series no. 65 of 19 March 2007)

- Italian Legislative Decree no. 85 of 19 May 2016 – "Implementation of Directive 2014/34/EU on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres";

- Law no. 1083 of 6 December 1971 - “Standards for the safe use of fuel gas”;

- UNI EN 228-1 – "Pipe threads where pressure-tight joints are not made on the thread - Designation, dimensions and tolerances";

- UNI EN 1092-1 – “Flanges and their joints - Circular flanges for pipes, valves, fittings and accessories, NP designated -Part 1: Steel flanges”

- UNI EN 682 – "Elastomeric seals. Requisites of elastomeric materials used in pipes and fittings carrying gas and hydrocarbon fluids";

- UNI EN 1359 -– "Diaphragm gas meters";

- UNI EN 1706 – "Aluminium and aluminium alloys - Castings - Chemical composition and mechanical properties";

- UNI 9036 – "Measuring units with deformable-wall meters. Installation requirements";

- UNI EN 10087 – "Free-cutting steels - Technical delivery conditions for semi-finished products, hot-rolled bars and rods";

- UNI EN 10130 – "Cold rolled low carbon steel flat products for cold forming – Technical delivery conditions";

- UNI EN 10152 – Electrolytically zinc-coated cold-rolled, steel flat products for cold forming – Technical delivery conditions";

- UNI EN 10346 – "Continuously hot dip coated steel flat products for cold forming – Technical delivery conditions";

- UNI EN 10216-1 – "Seamless steel tubes for pressure purposes – Technical delivery conditions - Part 1: Non-alloy steel tubes for use at room temperature";

- UNI EN 10297 – "Seamless circular steel tubes for mechanical and general engineering purposes - Technical delivery conditions";

- Legislative Decree no. 84 of 19 May 2016 - "Implementation of Directive 2014/32/EU on the harmonisation of the laws of Member States relating to the making available on the market of measuring instruments, as amended by Directive (EU) 2015/13”;

- Circular no. 3620 of 22 October 2008 – "Guidance on the interpretation of the provisions of Legislative Decree no. 22 of 2 February 2007, implementing Directive 2004/22/EC";

- Ministerial Decree no. 93 of 21 April 2017, as amended and supplemented – "Regulation concerning the criteria for performing subsequent metrological checks on gas meters and volume conversion devices, pursuant to Legislative Decree no. 84 of 19 May 2016 "Implementation of Directive 2014/32/EU" on measuring instruments (MID);

- Italian Legislative Decree no. 81 of 9 April 2008, as amended and supplemented – Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace;

- UNI CEI EN ISO/IEC 17050-1 - "Conformity assessment - Supplier's declaration of conformity - Part 1: General requirements”;

- LAW no. 99 of 23 July 2009 "Provisions for the development and internationalisation of enterprises, as well as on energy";

- Legislative Decree no. 206 of 06 September 2005, as amended and supplemented - "Consumer code, pursuant to Article 7 of Law no. 229 of 29 July 2003."

# APPENDICES

- APPENDIX 1 – "Meter model 6 m3/h (G4)”

- APPENDIX 2 – "Meter model 10 m3/h (G6)”

- APPENDIX 3 – "Meter model 16 m3/h (G 10)”

- APPENDIX 4 – "Meter model 25 m3/h (G 16)”

- APPENDIX 5 – "Meter model 40 m3/h (G 25)”

- APPENDIX 6 – "Meter model 65 m3/h (G 40)”

- APPENDIX 7 – "Meter model 100 m3/h (G 65)”

- APPENDIX 8 – "Meter model 160 m3/h (G 100)”

- APPENDIX 9 – "Meter model 4 m3/h (G 2.5)”

- APPENDIX 10 – "Construction details codified by Italgas Reti"

- APPENDIX 11 – “Sample declaration of conformity with this technical specification”

- APPENDIX 12 – “Sample declaration of exclusion from Directive 2014/34/EU”

# Annex

S.T.V.F.C. 2945300 – "Synthetic rubber seals".

## APPENDIX 1

METER MODEL 6 m3/h (G 4)

(Normally used only for LPG)

Material code: 2401025

TECHNICAL CHARACTERISTICS:

- maximum flow rate (Qmax): 6 m3/h

- minimum flow rate (Qmin): 0.040 m3/h

- maximum operating pressure:  50 kPa (0.5 bar)

- p at maximum flow rate:  0.2 kPa (2 mbar)

DIMENSIONS: shown on drawing in mm

METROLOGICAL REQUIREMENTS: UNI EN 1359

MARKING: (CE-MID 2014/32/EU).

MATERIALS:

- BODY: steel UNI EN 10130, UNI EN 10152, UNI EN 10346 (alternative: aluminium UNI EN 1706)

- DIAPHRAGM: synthetic fabric (coded as per Appendix 10)

NUMERICAL INTEGRATOR: Compliant with UNI EN 1359 and fitted with a magnet for activating a low-frequency pulse emitter (reed) with resolution 1 imp = 0.01 m3

CLOCK BOX: prepared with pocket, for subsequent insertion of the Low Frequency pulse emitter.

PROTECTIVE COATING: compliant with UNI EN 1359 point 6.3.

FITTING: male "gas" threaded cylindrical fittings UNI EN ISO 228-1

## APPENDIX 2

METER MODEL 10 m3/h (G 6)

(Normally used only for LPG)

Material code: 2401032

TECHNICAL CHARACTERISTICS:

- maximum flow rate (Qmax): 10 m3/h

- minimum flow rate (Qmin): 0.060 m3/h

- maximum operating pressure:  50 kPa (0.5 bar)

- p at maximum flow rate:  0.2 kPa (2 mbar)

DIMENSIONS: shown on drawing in mm

METROLOGICAL REQUIREMENTS: UNI EN 1359

MARKING: (CE-MID 2014/32/EU).

MATERIALS:

- BODY: steel UNI EN 10130, UNI EN 10152, UNI EN 10346 (alternative: aluminium UNI EN 1706)

- DIAPHRAGM: synthetic fabric (coded as per Appendix 10)

NUMERICAL INTEGRATOR: Compliant with UNI EN 1359 and fitted with a magnet for activating a low-frequency pulse emitter (reed) with resolution 1 imp = 0.01 m3

CLOCK BOX: prepared with pocket, for subsequent insertion of the Low Frequency pulse emitter.

PROTECTIVE COATING: compliant with UNI EN 1359 point 6.3.

FITTING: male "gas" threaded cylindrical fittings UNI EN ISO 228-1

## APPENDIX 3

METER MODEL 16 m3/h (G 10)

(Normally used only for LPG)

Material code: 2401042

TECHNICAL CHARACTERISTICS:

- maximum flow rate (Qmax): 16 m3/h

- minimum flow rate (Qmin): 0.100 m3/h

- maximum operating pressure:  50 kPa (0.5 bar)

- p at maximum flow rate:  0.2 kPa (2 mbar)

DIMENSIONS: shown on drawing in mm

METROLOGICAL REQUIREMENTS: UNI EN 1359

MARKING: (CE-MID 2014/32/EU).

MATERIALS:

- BODY: steel UNI EN 10130, UNI EN 10152, UNI EN 10346 (alternative: aluminium UNI EN 1706)

- DIAPHRAGM: synthetic fabric (coded as per Appendix 10)

NUMERICAL INTEGRATOR: Compliant with UNI EN 1359 and fitted with a magnet for activating a low-frequency pulse emitter (reed) with resolution 1 imp = 0.1 m3

CLOCK BOX: prepared with pocket, for subsequent insertion of the Low Frequency pulse emitter.

PROTECTIVE COATING: compliant with UNI EN 1359 point 6.3.

THERMOWELL AND PRESSURE INTAKE: See point 4.2.

FITTING: male "gas" threaded cylindrical fittings UNI EN ISO 228-1

## APPENDIX 4

METER MODEL 25 m3/h (G 16)

(Normally used only for LPG)

Material code: 2401052

TECHNICAL CHARACTERISTICS:

- maximum flow rate (Qmax): 25 m3/h

- minimum flow rate (Qmin): 0.160 m3/h

- maximum operating pressure:  50 kPa (0.5 bar)

- p at maximum flow rate:  0.3 kPa (3 mbar)

DIMENSIONS: shown on drawing in mm

METROLOGICAL REQUIREMENTS: Compliant with UNI EN 1359

MARKING: (CE-MID 2014/32/EU).

MATERIALS:

- BODY: steel UNI EN 10130, UNI EN 10152, UNI EN 10346 (alternative: aluminium UNI EN 1706)

- DIAPHRAGM: synthetic fabric (coded as per Appendix 10)

NUMERICAL INTEGRATOR: Compliant with UNI EN 1359 and fitted with a magnet for activating a low-frequency pulse emitter (reed) with resolution 1 imp = 0.1 m3

CLOCK BOX: prepared with pocket, for subsequent insertion of the Low Frequency pulse emitter.

PROTECTIVE COATING: compliant with UNI EN 1359 point 6.3.

THERMOWELL AND PRESSURE INTAKE: See point 4.2.

FITTING: male "gas" threaded cylindrical fittings UNI EN ISO 228-1

## APPENDIX 5

METER MODEL 40 m3/h (G 25)

(Normally used only for LPG)

Material code: 2401062

TECHNICAL CHARACTERISTICS:

- maximum flow rate (Qmax): 40 m3/h

- minimum flow rate (Qmin): 0.250 m3/h

- maximum operating pressure:  50 kPa (0.5 bar)

- p at maximum flow rate:  0.3 kPa (3 mbar)

DIMENSIONS: shown on drawing in mm

METROLOGICAL REQUIREMENTS: Compliant with UNI EN 1359

MARKING: (CE-MID 2014/32/EU).

MATERIALS:

- BODY: steel UNI EN 10130, UNI EN 10152, UNI EN 10346

- DIAPHRAGM: synthetic fabric (coded as per Appendix 10)

NUMERICAL INTEGRATOR: Compliant with UNI EN 1359 and fitted with a magnet for activating a low-frequency pulse emitter (reed) with resolution 1 imp = 0.1 m3

CLOCK BOX: prepared with pocket, for subsequent insertion of the Low Frequency pulse emitter.

PROTECTIVE COATING: compliant with UNI EN 1359 point 6.3.

THERMOWELL AND PRESSURE INTAKE: See point 4.2.

FITTING: male "gas" threaded cylindrical fittings UNI EN ISO 228-1

## APPENDIX 6

METER MODEL 65 m3/h (G 40)

Material code: 2401072

TECHNICAL CHARACTERISTICS:

- maximum flow rate (Qmax): 65 m3/h

- minimum flow rate (Qmin): 0.400 m3/h

- maximum operating pressure:  50 kPa (0.5 bar)

- p at maximum flow rate:  0.3 kPa (3 mbar)

DIMENSIONS: shown on drawing in mm

METROLOGICAL REQUIREMENTS: UNI EN 1359

MARKING: (CE-MID 2014/32/EU).

MATERIALS:

BODY: sheet steel UNI EN 10130, UNI EN 10152, UNI EN 10346

- SECTIONS: steel UNI EN 10216 or UNI EN 10087, UNI EN 10297

- FLANGE: steel NP 16

- DIAPHRAGM: synthetic fabric (coded as per Appendix 10)

NUMERICAL INTEGRATOR: Compliant with UNI EN 1359 and fitted with a magnet for activating a low-frequency pulse emitter (reed) with resolution 1 imp = 0.1 m3

CLOCK BOX: prepared with pocket, for subsequent insertion of the Low Frequency pulse emitter.

PROTECTIVE COATING: compliant with UNI EN 1359 point 6.3.

THERMOWELL AND PRESSURE INTAKE: See point 4.2.

FITTING: steel flanges with support ring NP 16, UNI EN 1092-1

## APPENDIX 7

METER MODEL 100 m3/h (G 65)

Material code: 2401082

TECHNICAL CHARACTERISTICS:

- maximum flow rate (Qmax): 100 m3/h

- minimum flow rate (Qmin): 0.650 m3/h

- maximum operating pressure:  50 kPa (0.5 bar)

- p at maximum flow rate:  0.4 kPa (4 mbar)

DIMENSIONS: shown on drawing in mm

METROLOGICAL REQUIREMENTS: Compliant with UNI EN 1359

MARKING: (CE-MID 2014/32/EU).

MATERIALS:

- BODY: sheet steel, UNI EN 10130, UNI EN 10152, UNI EN 10346

- SECTIONS: steel UNI EN 10216 or UNI EN 10087, UNI EN 10297

- FLANGE: steel NP 16

DIAPHRAGM: synthetic fabric (coded as per Appendix 10)

NUMERICAL INTEGRATOR: Compliant with UNI EN 1359 and fitted with a magnet for activating a low-frequency pulse emitter (reed) with resolution 1 imp = 1 m3

CLOCK BOX: prepared with pocket, for subsequent insertion of the Low Frequency pulse emitter.

PROTECTIVE COATING: compliant with UNI EN 1359 point 6.3.

THERMOWELL AND PRESSURE INTAKE: See point 4.2.

FITTING: steel flanges with support ring NP 16, UNI EN 1092-1

## APPENDIX 8

METER MODEL 160 m3/h (G 100)

Material code: 2401092

TECHNICAL CHARACTERISTICS:

- maximum flow rate (Qmax): 160 m3/h

- minimum flow rate (Qmin): 1 m3/h

- maximum operating pressure:  50 kPa (0.5 bar)

- p at maximum flow rate:  0.4 kPa (4 mbar)

DIMENSIONS: shown on drawing in mm

METROLOGICAL REQUIREMENTS: UNI EN 1359

MARKING: (CE-MID 2014/32/EU).

MATERIALS:

- BODY: steel UNI EN 10130, UNI EN 10152, UNI EN 10346

- FLANGES: steel NP 16

- DIAPHRAGM: synthetic fabric (coded as per Appendix 10)

NUMERICAL INTEGRATOR: Compliant with UNI EN 1359 and fitted with a magnet for activating a low-frequency pulse emitter (reed) with resolution 1 imp = 1 m3

CLOCK BOX: prepared with pocket, for subsequent insertion of the Low Frequency pulse emitter.

PROTECTIVE COATING: compliant with UNI EN 1359 point 6.3.

THERMOWELL AND PRESSURE INTAKE: See point 4.2.

FITTING: steel flanges with support ring NP 16, UNI EN 1092-1

## APPENDIX 9

METER MODEL 4 m3/h (G 2.5) FOR LPG

Material code: 2401012

TECHNICAL CHARACTERISTICS:

- maximum flow rate (Qmax): 4 m3/h

- minimum flow rate (Qmin): 0.00625 m3/h

- maximum operating pressure:  50 kPa (0.5 bar)

- p at maximum flow rate:  0.2 kPa (2 mbar)

DIMENSIONS: shown on drawing in mm

METROLOGICAL REQUIREMENTS: UNI EN 1359

MARKING: (CE-MID 2014/32/EU).

MATERIALS:

- BODY: steel, UNI EN 10130, UNI EN 10152, UNI EN 10346 (alternative: aluminium UNI EN 1706)

- DIAPHRAGM: synthetic fabric (coded as per Appendix 10)

NUMERICAL INTEGRATOR: Compliant with UNI EN 1359 and fitted with a magnet for activating a low-frequency pulse emitter (reed) with resolution 1 imp = 0.01 m3

CLOCK BOX: prepared with pocket, for subsequent insertion of the Low Frequency pulse emitter.

PROTECTIVE COATING: compliant with UNI EN 1359 point 6.3.

FITTING: male "gas" threaded cylindrical fittings UNI EN ISO 228-1

## APPENDIX 10

Construction specifications codified by Italgas Reti

| Code | DESCRIPTION |
| --- | --- |
| 01 | SIREX SYNTHETIC DIAPHRAGM |
| 02 | ROBET SYNTHETIC DIAPHRAGM |
| 03 | REEVES SYNTHETIC DIAPHRAGM |
| 04 | METFLEX 7M95 SYNTHETIC DIAPHRAGM |
| 05 | METFLEX MFP 343 SYNTHETIC DIAPHRAGM |
| 06 | HELSATECH 8410 DIAPHRAGM |
| 10 | ELECTRONIC TOTALISER |
| 11 | LF PULSE EMITTER |
| 12 | ENCODER |
| 21 | SYREX PRED. L.F. P.E DIAPHRAGM |
| 22 | BOBET PRED. L.F. P.E DIAPHRAGM |
| 23 | REEVES PRED. L.F. P.E DIAPHRAGM |
| 24 | METFLEX 7M95 PRED. L.F. P.E DIAPHRAGM |
| 25 | METFLEX MFP 343 PRED. L.F. P.E DIAPHRAGM |
| 26 | HELSATECH 8410 PRED. L.F. P.E DIAPHRAGM |
| 27 | EFFBE PRED. L.F. P.E DIAPHRAGM |

## APPENDIX 11

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN ISO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

(4)	The following products manufactured by us:

| Our material code (5) | Italgas Reti material code (6) |
| --- | --- |
| xxx | 2401025 |
| xxx | xxx |

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(7)	S.T.V.F.C. 2401300	DIAPHRAGM METERS FOR METHANE GAS AND LPG Edition 1 of 15/06/2017

Additional information:

(8) 	...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(9) 	............................................................. 			......................................................................................................................

(Name and position) 						(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number).

- The person issuing the Declaration (Supplier) must be unequivocally specified.

- The “subject” must be unambiguously described so that the declaration of conformity can be referred to the subject in question.

- List all the products for which company use authorisation is being requested.

- For each individual product supplied, state the material code used by the Supplier.

- For each individual product supplied, please quote the material code assigned by Italgas Reti, which can be found in the Italgas Reti reference documents. If there are none, please contact SERTEC-NORM.

- Include references to the Italgas Reti documents for the proposed products.

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1).

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

## APPENDIX 12

ATEX Exclusion Declaration

We ..............................................................................................................................................................

(name of organisation)

with registered office in .............................................................................................................

(address)

as the .................................................................................................................................................

(Manufacturer / Authorised Representative)

declare under our sole responsibility that the products series

.....................................................................................................................................................................

.....................................................................................................................................................................

.....................................................................................................................................................................

(name, type or model, batch, group or serial numbers)

described in the Technical Specification / document(s)

.....................................................................................................................................................................

.....................................................................................................................................................................

(when necessary)

to which this declaration refers, comply with the following legislative / regulatory document(s)

.....................................................................................................................................................................

.....................................................................................................................................................................

(title(s) and/or number(s) and date(s) of publication of the standard(s) or other legislative and/or regulatory document(s))

and, according to Article 1, subsection 1a) of Directive 2014/34/EU of 26 February 2014 (Legislative Decree no. 85 of 19 May 2016) and Chapter 1 of ATEX 2014/34/EU GUIDELINES (first edition), based on an ATEX analysis (see paragraph 32 of the aforementioned ATEX 2014/34/EU GUIDELINES), do not fall within the scope of the Directive 2014/34/EU, as they do not risk causing an explosion due to the lack of potential ignition sources as defined in Standard UNI EN 1127-1, when used in systems that comply with the following legislative and/or regulatory documents

.....................................................................................................................................................................

.....................................................................................................................................................................

.....................................................................................................................................................................

(title and/or number and date of publication of legislative and/or regulatory documents)

They can therefore be installed in all types of zones as defined in Legislative Decree no. 81 of 9 April 2008, as amended, Title XI (Directive 1999/92/EC of 16 December 1999).

.................................................................. 		..................................................................................................................................

(place and date of issue)				(name and signature or equivalent stamp of authorised person)

In the case of processing peaks, in which case SERTEC/LAB will promptly inform the Supplier and HSEQ, the check will be carried out within a maximum of ten working days.

Supplier means the party responsible for the design and construction of the products or its legal representative as defined in Legislative Decree no. 206 of 6 September 2005, as amended and supplemented. - "Consumer code, pursuant to Article 7 of Law no. 229 of 29 July 2003."