“TECHNICAL SPECIFICATION”

S.T. TC-1/682

Automated system for gas volume measurement

| Compiled by | APT-ATECH-NORM | MARELLA, MANUELE |
| --- | --- | --- |
|  | APT-METER-MCG | PICONE, GIUSEPPE |
| Checked by | APT-ATECH-NORM | CIMINO, SALVATORE |
| Checked by | BLUDIGIT-IOTEP | ROLETTO, ALESSANDRO |
| Checked by | BLUDIGIT-ARCHI | RATTO, MARCO |
| Checked by | BDT | AMBROSI, LEONARDO |
| Checked by | BLUDIGIT-CYBER | TONELLO, LORENZO |
| Checked by | PROMA/CMMAT | FASSINO, SILVIO |
| Checked by | PROMA-MATMA | SCOTTO, ENRICO |
| Checked by | HSEQ | LIMONTA, AGOSTINO MASSIMO |
| Checked by | APT-ATECH | GHIBAUDO, CLAUDIO |
| Approved by | APT | LACIDOGNA, SANDRO |

SUMMARY

1	PRELIMINARY INFORMATION	4

1.1	Cancels and replaces	4

1.2	Reason for issue	4

1.3	Company departments mentioned in the document	4

1.4	Definitions	4

2	PURPOSE AND FIELD OF APPLICATION	4

2.1	Purpose	4

2.2	Field of application	4

3	SPECIFICATIONS	5

4	Introduction to the AUTOMATED MEASUREMENT system	6

5	TECHNICAL CHARACTERISTICS  Type 2 device	7

5.1	Measurement cabinet and accessories	8

5.1.1	Mechanical characteristics	8

5.1.2	Sundry accessories and components	9

5.1.3	Wiring and interconnections	10

5.1.4	Earthing connections	11

5.2	Type 2 electronic gas volume conversion device	11

5.2.1	Electronic gas volume conversion device for volumetric measurement systems	11

5.2.2	Electronic gas volume conversion device for venturimetric measurement systems	15

5.3	Intrinsically safe barriers	17

5.4	Remote reading module	17

5.4.1	Industrial 4G/2G modem/router	18

5.5	Electrical power supply unit with integrated UPS	19

6	Technical characteristics TYPE 1 DEVICE	19

6.1	TECHNICAL CHARACTERISTICS OF THE TYPE 1 GAS VOLUME CONVERSION DEVICE	20

6.2	REMOTE POWER SUPPLY MODULE	22

6.3	CONNECTION CABLES	25

6.3.1	Input signals and connection to the remote reading module	25

6.3.2	Earthing	26

7	TECHNICAL CHARACTERISTICS data LOGGER	27

7.1	DATA LOGGER ELECTRONIC BACK-UP DEVICE (FF TYPE 1)	27

7.2	REMOTE POWER SUPPLY MODULE	29

7.3	CONNECTION CABLES	29

7.3.1	Input signals and connection to the remote reading module	29

7.3.2	Earthing	30

8	POWER SUPPLY UNIT for Chapter 6 and 7 devices only	31

9	Security of electronic devices	33

10	Technical assessment	34

11	Marking	34

12	TYPE TEST	35

12.1	Supplier	35

12.2	Documents to be submitted	35

12.3	Test Documentation	35

12.4	Supply Documentation	35

13	TESTS AND INSPECTIONS	36

13.1	Right of the Client	36

14	CONDITIONS OF SUPPLY	36

15	PRODUCT WARRANTY	36

16	REFERENCE STANDARDS	37

17	APPENDICES	39

APPENDIX 1	40

APPENDIX 2	42

# PRELIMINARY INFORMATION

## Cancels and replaces

This specification cancels and replaces:

- S.T.V.F.C. TC-1/682 "Computerised gas volume measurement system” Edition no. 1 of 15 June 2017.

## Reason for issue

The update of the Technical Specification TC-1/ 682 and edition in the form of a Technical Specification (T.S.), became necessary as a result of:

- issuing of new national and European standards (e.g. UNI 9167-3, UNI TS 11629, etc.);

- differentiation of the technical/functional characteristics of the Type 1 and Type 2 conversion devices;

- addition of data logger requirements;

- inclusion of IT security criteria;

- new organisational set-up.

## Company departments mentioned in the document

- PROMA-CMMAT = Category Manager Materials

## Definitions

For definitions of the technical terms used in this specification, please refer to the relevant regulations, a non-exhaustive list of which can be found in Chapter 16.

# PURPOSE AND FIELD OF APPLICATION

## Purpose

The purpose of this T.S. is to define the technical characteristics of the type 1 and type 2 automated measurement  systems, the procedures for carrying out the technical inspections for approval for company use and the criteria for the supply and testing of an automated measurement system as defined below.

## Field of application

This Technical Specification applies, in the case of direct purchase by Italgas Reti, whenever a material covered by this specification must be approved for company use, produced by a new potential Supplier  or by an existing Supplier.

# SPECIFICATIONS

- This specification must be understood as an integral part of the "ASSESSMENT AND QUALIFICATION SYSTEM FOR SUPPLIERS OF ITALGAS."

- This specification contains the minimum technical requirements demanded by Italgas Reti based on the reference legislative and technical standards.

- It is the Supplier's responsibility to ensure that the products supplied fully comply with the provisions of this technical specification and the applicable standards.

- If the materials in question are supplied by an installer, the installer must document their compliance as required under “Documentation required from the Supplier”.

- It is the Supplier's responsibility, during the product design, production and control process, to verify that there are no construction faults in the finished products (e.g. sharp edges, incorrect directions for use and maintenance, etc.), which may jeopardise the health and safety of the Client's workers in relation to the provisions of Legislative Decree no. 81/08, as amended and supplemented.

- For all technical and operational aspects that conflict with or are not mentioned in this technical specification but that nevertheless pertain to the design, installation, maintenance and use of the products themselves, it is the Supplier's responsibility to refer to the regulations in force.

- Each Supplier may also be approved for company use for one or more types of equipment described in this T.S.

# Introduction to the AUTOMATED MEASUREMENT system

In this T.S., an automated measurement system is understood to be the set of devices attributable to flow-computers/volume converters and data loggers.

The automated measurement system may be type 1 for Qero<= a 4,000 smc/h or type 2 for higher flow rates. In both cases, the system must be Class II to allow connection to the quality system QS (quality analyser / gas chromatograph).

The data-logger must be type 1 and class I.

# TECHNICAL CHARACTERISTICS  Type 2 device

The type 2 flow-computer is subject to Law no. 186 of 1 March 1968, relating to the realisation and construction of materials, equipment, machinery, installations and electrical and electronic systems “to standard”; it must therefore be suitable for the intended use and ensure, as regards the materials used and their construction, adequate resistance to the environmental and mechanical factors to which they may be exposed during operation.

It is also subject to a whole series of legislative provisions, in relation to the required characteristics, materials and intended use, a non-exhaustive list of which is provided in point 16 of this T.S. It must also comply with any further requirements/provisions defined by the Network Code of the Supplier (Transporter).

Unless explicitly referred to otherwise, the standards cited are those in the latest edition, including any variants/updates and/or corrigenda published.

The constituent elements of a type 2 flow computer are summarised in the table below:

Constituent elements of a type 2 flow computer

Measurement cabinet and accessories

Electronic gas volume conversion device

Intrinsically safe barriers

ITG Remote Reading Module

Electrical power supply unit with integrated UPS

Table  1: Constituent elements of a type 2 flow-computer

The technical characteristics of the individual elements listed in the table above are indicated in the following paragraphs.

## Measurement cabinet and accessories

The measurement cabinet must be sized to contain an electronic gas volume conversion device, intrinsically safe barriers, a Remote reading module, an electrical power supply unit with integrated UPS and all the accessories required for the correct operation of the automated measurement system, with a minimum reserve of 30%.

The measurement cabinet must be suitable for wall mounting and must therefore be equipped with all the necessary mounting accessories. If the measurement cabinet should contain more than one electronic gas volume conversion device or other equipment other than that indicated in Table  1 as a result of special design requirements, it is up to the Supplier to verify the solution with a wall-mounted cabinet or to propose the solution with a Rack 19" floor-standing cabinet to be evaluated by the Client at the tender stage, with the need to minimise overall dimensions.

The measurement cabinet must be installed in a "non-hazardous location" (in relation to explosive atmospheres due to the presence of gas), in accordance with CEI EN 60079- 10-1, inside a dedicated room and must comply  with the CEI EN 62208, CEI EN 61439-1 standards and have a mechanical protection rating of not less than IP 44, in accordance with CEI EN 60529, and a strength rating of IK 09 (min.), in accordance with CEI EN 62262.

### Mechanical characteristics

The measurement cabinet must have the following mechanical characteristics:

- small dimensions and weight compatible with the installation requirements based on the type of system requested in the order, aimed at minimising installation, commissioning and maintenance costs;

- it must be self-supporting and composed of press-moulded and welded, pickled, passivated sheet steel panels with a minimum thickness of 12/10 mm in light grey RAL 7035 epoxy paint with a "fine textured" finish;

- inner surface treated with anti-condensation material;

- inspectable from the front by means of a transparent door made of anti-reflective and UV-resistant polymethylmethacrylate at least 3 mm thick and fitted with hinges permitting 180° opening and closing handles, hinged on both the right and left sides, preferably double to allow full opening even in confined spaces;

- sealable, inner counter-door, suitably hinged to allow access to internal parts for normal maintenance, on which the user interface unit is present, located on the transparent door;

- sealable protective cover of acquired field metrological signals/measurements (transducers, meter, QS, etc.);

- cable entry possible from the bottom of the panel through easily drilled panels complete with cable glands;

- support plate, fixed to the rear wall, for terminal blocks, intrinsically safe barriers, etc., which can be accessed by opening the inner counter-door;

- strips of interconnecting cables between switches and equipment located on the panels and terminal blocks, contained in special self-extinguishing sheaths;

- cable ducts, DIN profiles and related terminal blocks mounted on plates;

- where possible, internal document pocket for tables, programming/configuration memos, various wiring diagrams for maintenance, etc.

### Sundry accessories and components

The measurement cabinet must have the following sundry accessories and components:

- warning signs appropriately placed and compliant with Legislative Decree 81/08 as amended and supplemented;

- mechanical and electrical protection complying with the CEI EN 60947 standard for each piece of equipment in the system that is to be individually protected and signalled;

- for the solution in a 19" Rack floor-standing cabinet, natural ventilation by means of dedicated slits and the possibility of implementing an air-conditioning system to guarantee optimal environmental conditions inside the cabinet, consisting of a fan-filter unit for forced ventilation and an anti-condensation heater, both placed in accessible positions and protected by a thermal-magnetic circuit breaker installed upstream of the thermal control device, controlled by a special thermo-hygrostat with a temperature regulation scale between 0 and +60°C and humidity between 30 and 90 RH%, with IPXXB (min.), suitable for DIN rail mounting, with LED indicators and 2.5 mm2 terminals;

- modules and IS barriers inserted in such a way as to allow inspection and easy access for replacement for calibrations, measurements (TEST) necessary for troubleshooting and preventive maintenance;

- input/output terminal blocks and wiring in general, suitably marked, protected against accidental contact, easily accessible and arranged in accordance with CEI EN 61439 and Law no. 186 of 1 March 1968: the terminal blocks, the connection system to the earth system and all cables used for intrinsically safe circuits must be mounted and marked in accordance with CEI EN 60079-0 and CEI EN 60079-11;

### Wiring and interconnections

The measurement cabinet must be supplied with all sections wired, even if not connected to equipment.

The wiring must use flexible cable, with very low emission of fumes and toxic gases, not propagating fire and with Uo/U rated voltages not exceeding 0.6/1 kV according to CEI 20-38 and must be divided into the following categories:

- Rated voltages at 12 VDC / 24 VAC;

- Rated voltages at 230 VAC.

The markings of the conductors connected to terminal blocks must comply with CEI EN 60445.

Each end of the conductor will be marked using both the symbol of the terminal to which it is connected and that of the terminal to which the other end is connected.

The marking of each end will be completed by the symbol of the terminal block, relay or equipment, etc. to which such end is connected.

The terminals will be marked with acronyms, progressive numbers and shown on the drawings.

In particular:

- the cables should, where possible, have a different colour according to the voltage level;

- the wiring must use flexible wire, with very low emission of fumes and toxic gases, fire-retardant and with Uo/U rated voltages not exceeding 0.6/1 kV;

- the conductor cross-sections must be suitable for the intended load;

- the conductor terminals must be fitted with a suitable cable lug and numbered with marking protected with transparent tube;

- splicing of cables will not be permitted;

- cables and ducts must not interfere with maintenance and equipment testing;

- interconnecting cables fitted with appropriate connectors to allow easy connection between terminal blocks and components inside the electrical panel;

- the cable shields should be connected to the equipotential bonding bar inside the panel, keeping the connection as short as possible. The shield should be earthed at one end only;

- the earthing conductors and terminals must be green/yellow;

- adequate protection must be provided, where necessary, on the terminals and normally live components inside the panel in order to prevent accidental contact by staff. The level of protection against direct contact must be definable according to the types of intervention and responsibility of the appointed personnel: visual inspection, standard configuration and calibration, fault repair and preventive maintenance.

### Earthing connections

An earthing bar (equipotential node) must be provided on the panel.

The closing doors and revolving frame, if considered a “mass”, must be connected by means of flexible cables of a suitable cross-section to the earthing bar (equipotential node).

All normally non-energised parts of the electrical equipment must be connected by means of a flexible cable to the earthing bar (equipotential node).

## Type 2 electronic gas volume conversion device

The gas volume conversion device, in addition to the specifications of the following paragraphs, must be supplied Class 2 or Class 3 on request, complying with UNI-TS 11629 and UNI-EN 12405-1. The electronic gas volume conversion device must also be able to receive from the quality analyser/gas chromatograph (please refer to the reference specification) the gas quality values including PCS for conversion operations (according to the calculation algorithm implemented). In this regard, the Class 2 and Class 3 electronic gas volume conversion devices must check the availability of quality data from the QS apparatus (Gas Chromatograph or Quality Analyser) at least every 2 min.

The electronic gas volume conversion device must be capable of acquiring pulses from both conventional meters (NCVNon Contact Voltage) and ultrasound meters ("OC" or Namur non-electrically isolated passive output)

The electronic gas volume conversion device must be suitable for installation in the measurement cabinet described in point 5.1 and must be suitable for the conversion of gas volumes in accordance with the type of measurement system communicated by the Client at the time of the request:

- volumetric measuring equipment (ultrasound or conventional technology meters);

- venturimetric measurement system.

### Electronic gas volume conversion device for volumetric measurement systems

The "Type 2" electronic gas volume conversion device must comply with UNI TS 11629, UNI EN 12405-1, UNI EN ISO 12213-1/2 or UNI EN ISO 12213-3 in compliance with Legislative Decree no. 22 of 2 February 2007, as amended and supplemented and therefore must:

- convert gas volumes, measured by ultrasound (see T.S. 9995305 Ed2) or turbine gas meters (see T.S.. 2401301) from operating conditions (Vm) to standard conditions (Vb) according to the calculation algorithm defined in the AGA REPORT #7;

- be designed for intrinsically safe connection with the following field transmitters:

  - have a relative or absolute pressure transmitter with reference accuracy of ±0.1% of the calibration SPAN or better with characteristics defined in the T.S. TC-1/631;

  - have high and/or low frequency (HF-LF) pulse signals based on those generated by the reference gas meter;

  - 3- or 4-wire Pt 100 temperature transmitter or thermoresistance with characteristics defined in the T.S. TC-1/631.

NOTE: The execution criteria for electrical wiring must comply with the current state-of-the-art WRMP (Ex-i protection method);

The "Type 2" electronic gas volume conversion device must also have the following main features (detailed features to be specified by the Supplier in the documentation accompanying the product):

- power supply from electrical power supply unit with integrated UPS;

- provision for connection to the printer, to be installed on the internal counter-door of the measurement  cabinet and to be supplied only if expressly requested by the Client;

- storage unit for controlling the remote reading module, which must be installed inside the electronic gas volume conversion device and equipped with an RS232 serial interface, as described in point 5.4;

- static type memory (e.g. Compact Flash, SD card or similar) which must contain events, hourly, daily and monthly data and which must be store at least the cubic metres at operating conditions and at reference conditions, the energy (when calculated) the maximum and minimum flow rates (daily) and period diagnostics, with an update interval of the static memory on a new event of not more than 15 min, and rewriting of the memory in cyclic mode, with data extraction by copying (fully automatically managed) the entire memory onto a portable medium;

- isolated analogue outputs (420 mA) with which the Client may choose to associate the following quantities (as a minimum): Instantaneous flow rate at standard conditions (QI1), measurement pressure (MP), temperature, etc.;

- isolated digital outputs (On/Off) which the Client may choose to configure as a count pulse output (e.g. gas volumes) or alarm output;

- RS-232/485 serial port implementing the MODBUS RTU/ASCII protocol, programmable for interfacing with gas chromatograph/gas quality analyser;

- provision of 4G/2G modem/router (see point 5.4.1);

- provision of an additional RS-485 or Ethernet serial interface port supporting MODBUS RTU or MODBUSTCP communication protocols for connection to the Italgas RTU locally and for the transfer of all non-fiscally valid data processed;

- provision of an additional RS-485 serial interface port supporting POT communication protocols for connection to the transporter's RIU (e.g. Snam RIU);

- additional RS-232 serial or Ethernet communication ports on which data can be downloaded via locally connected portable devices, configuration/maintenance operations can be performed via external devices, etc.;

- the Client reserves the right to request that an additional RS-485 serial port be provided with MODBUS RTU protocol and with metrological certification for connection to the relative ultrasound meter; the converter will therefore be able to use the input data to calculate the volumes in transit; it must also be possible to acquire the diagnostic values (e.g. metrological and non-metrological alarms/errors) that may be transmitted by the meter and made available on appropriate MODBUS registers in read-only mode for Italgas RTU 104;

- keyboard and display for programming all constants and displaying, on demand, input variables and processed values;

- possibility of periodic self-testing of the accuracy of all the variables with signalling of any out of limits;

- alarm signals for Calculator Fault (CF), Calculator mains failure (CMF), Calculator battery low (CB), out-of-scale inputs, etc., with voltage-free contacts for remote re-transmission of such alarms;

- software of the electronic gas volume conversion device in accordance with the requirements of WELMEC 7.2: Software Guide (MID).

In gas measurement systems where the Client states the need for the installation of a second volume converter, it reserves the right to consider the possibility of supplying dual-channel volume converters, instruments capable of simultaneously acquiring pulses, pressure, temperature from two different measurement lines and simultaneously processing the volumes.

The solutions indicated must be quoted at the tender stage.

Below is a summary of the required ports:

| Electronic gas volume conversion device for venturimetric measurement systems Port type | Communication Protocol | Number | Mandatory |
| --- | --- | --- | --- |
| RS232 | serial | 2 | YES |
| RS 485 | POT | 2 | YES |
| RS 485 | MODBUS | 1 | YES |
| RS 485/ethernet | MODBUS | 1 | YES |
| RS 485 | MODBUS (Metrological) | 1 | NO (on request) |

The "Type 2" electronic gas volume conversion device must comply with UNI TS 11629, UNI EN 12405-1, UNI EN ISO 12213-1/2 or UNI EN ISO 12213-3 and UNI EN ISO 5167-1/2 and must therefore:

- calculate gas volumes under reference conditions for differential pressure flow rate measurement equipment, integrating over time the natural gas flow rate determined with the formula derived from UNI EN ISO 5167-1;

- be designed for intrinsically safe connection with the following field transmitters:

  - have a relative or absolute pressure transmitter with reference accuracy of ±0.1% of the calibration SPAN or better with characteristics defined in the T.S. TC-1/631;

  - high (hdpT) and low (ldpT) differential pressure transmitter with reference accuracy of ±0.1% of calibration SPAN or better with characteristics defined in the T.S. TC-1/631;

  - 3- or 4-wire Pt 100 temperature transmitter or thermoresistance with characteristics defined in the T.S. TC-1/631.

NOTE: The execution criteria for electrical wiring must comply with the current state-of-the-art WRMP (Ex-i protection method);

The "Type 2" electronic gas volume conversion device must also have the following main features:

- power supply from electrical power supply unit with integrated UPS;

- provision for connection to the printer, to be installed on the internal counter-door of the measurement  cabinet and to be supplied only if expressly requested by the Client;

- storage unit for controlling the remote reading module, integrated in the electronic gas volume conversion device, as described in point 5.4;

- the automatic selection between the high and low differential signals for performing calculations must be programmable so that the high differential signal is used for values 80%  95% of the low differential signal;

- static type memory (e.g. Compact Flash, SD card or similar) which must contain events, hourly, daily and monthly data and which must be store at least the m3 at operating conditions and at reference conditions, the energy (when calculated) the maximum and minimum flow rates (daily) and period diagnostics, with an update interval of the static memory on a new event of not more than 15 min, and rewriting of the memory in cyclic mode, with data extraction by copying (fully automatically managed) the entire memory onto a portable medium;

- isolated analogue outputs (420 mA) with which the Client may choose to associate the following quantities (as a minimum): Instantaneous flow rate at standard conditions (QI1) and relative gas density (GY), etc.;

- isolated digital outputs (On/Off) which the Client may choose to configure as a count pulse output or alarm output;

- RS-232/485 serial port implementing the MODBUS RTU/ASCII protocol for interfacing with gas chromatograph;

- serial or Ethernet communication ports on which data can be downloaded via portable devices, configuration/maintenance operations can be performed via external devices, etc.

- keyboard and display for programming all constants and displaying, on demand, input variables and processed values;

- possibility of periodic self-testing of the accuracy of all the variables with signalling of any out of limits;

- alarm signals for Calculator Fault (CF), Calculator mains failure (CMF), Calculator battery low (CB), out-of-scale inputs, etc., with voltage-free contacts for remote re-transmission of such alarms;

If the type of plant requires the measurement of more than one line, the Supplier must check and indicate according to the type of product offered, whether it is necessary to use one or two separate electronic gas volume conversion devices and whether to double the number of pressure transmitters (relative or absolute pressure and high (hdpT) and low (ldpT) differential pressure).

In both cases, three analogue signals proportional to the corrected instantaneous flow rates QI1, QI2 and relative density (GY) respectively must also be provided.

## Intrinsically safe barriers

The electronic pressure transmitter, the electronic temperature transmitter (or the 3-wire or 4-wire Pt 100 thermoresistance) and the pulse emitter of the gas meter must be connected to the intrinsically safe barriers, the characteristics of which depending on the type of application envisaged are described in the T.S. TC-1/561, installed on the DIN rail inside the measurement cabinet.

Intrinsically safe barriers must be properly sealed inside the measurement cabinet.

The input parameters of field instruments, the output parameters of intrinsically safe barriers, the cables to be used, according to the T.S. IE-1/501, etc. must be such that the analysis of the intrinsically safe system(s) in accordance with CEI EN 60079-25 is verified.

It is the Supplier's responsibility to compile an "intrinsically safe system description document" containing all the information required to construct an adequately safe system.

## Remote reading module

The electronic gas volume conversion device must be equipped with a remote reading module for remote communication of signals and alarms by means of the following options:

- DIN-rail coupled industrial modem/router supporting communication transmission standards up to at least 4G and in downgrade 2G.

The communication protocol must comply with UNI/TS 11629.

### Industrial 4G/2G modem/router

The Modem/Router must be industrial grade, and comply with Legislative Decree no. 128 of 22 June 2016 concerning the implementation of Directive 2014/53/EU (RED Directive) on the harmonisation of the laws of the Member States relating to the making available on the market of radio equipment.

The 4G modem must have the following main characteristics:

- be suitable for use in DATA transmission applications;

- have compact dimensions and suitable for mounting inside the measurement cabinet;

- have a self-diagnosis circuit with auxiliary malfunction signals on status LEDs (power on, mains connection and field signal);

- it must support the function for receiving telephone calls in CSD data mode;

- modem firmware update via serial port;

- state-of-the-art integrated circuits that offer high standards of energy efficiency;

- antenna and connection cable included in the supply;

- SIM card reader at the following operating voltages 5V, 3V and 1.8V according to ISO/IEC 7816-3;

- RS232 serial interface provided for connection to the electronic gas volume conversion device;

- power supply from electrical power supply unit with integrated UPS.

- Communication Standard: 3GPP Release 11, 4G CAT 1 -7 and above and 3GPP Release GSM

- Transmission Rate: 300 Mbps / 100 Mbps (theoretical value that may vary depending on the operator);

- Network Frequency Band: B1 / B3 / B7 / B8 / B20 / B28 / B32 / B38, GSM: 900/1800 MHz;

- SMA-type connector for connection with external antenna;

- antenna and connection cable included in the supply;

- 10/100 Mbps Ethernet LAN port, meeting IEEE 802.3, IEEE 802.3u standard and supporting auto MDI/MDIX

- support for IPV4 and IPV6;

- DNS management;

- management of the following security features: firewall, DoS attack prevention, MAC address filters, VPN IPSEC, etc.;

- support for communication with POT and Old (former Snam) protocols;

## Electrical power supply unit with integrated UPS

The electrical power supply unit with integrated UPS consists of a power supply unit, batteries, stabilisers, filters, and is designed to guarantee autonomy in accordance with UNI TS 11629. The Client is however entitled to request 24-hour autonomy of the entire system in the event of a power failure in coordination with the QS.

The unit must have the following features and components:

- be suitable for mains supply voltage 230 VAC ±15% at 50 Hz ±5%;

- have electrical protections sized and aligned on all input and output circuits;

- protection against line surges - on the supply side - with protective devices (SPDs) complying with T.S. TC-1/706;

- filter to prevent the emission of radio interference in accordance with CEI 303-13;

- stabilised power supply switching filtered with the above-mentioned filters, which must be able to supply all the field instrumentation in intrinsically safe execution up to the maximum possible configuration in each type of measurement, including the electronic gas volume conversion device, the remote reading module, the analogue and/or digital outputs, the auxiliary circuits, etc.; these external power supplies must not constitute an overload or in any way compromise the performance of the system;

- Digital outputs for signalling mains power failure and low battery.

For the 19" Rack floor-standing cabinet version, this unit must comply with CEI 22-32, CEI 103-1/11 and must have the features and components listed below:

- safety transformer complying with CEI EN 61558-1 (CEI 96-3) and with a saturable core suitably sized to prevent incorrect tripping of upstream protections when mains power returns (power-up overcurrents);

- power supply with self-regulating circuits in both voltage and current and with protection filters;

- programmable thresholds for signalling excessive, insufficient or absent mains supply voltage with voltage-free contacts for remote re-transmission of generated signals;

- pre-alarm, alarm and total lockout thresholds (with manual reset) connected to back-up batteries with "self-test" circuit on battery function and voltage-free contacts for remote re-transmission of generated signals.

Italgas Reti is entitled to request, at the purchase stage, that by means of differentiated input, the necessary energy be obtained from photovoltaic panels with relative batteries. The sizing of such an alternative power supply unit shall be carried out exclusively on the basis of precise technical specifications produced by the Supplier of the equipment, who shall assume overall responsibility for the same.

# Technical characteristics TYPE 1 DEVICE

The "Type 1" electronic gas volume conversion device must comply with UNI EN 12405-1, UNI EN ISO 12213-1/2 or UNI EN ISO 12213-3 in compliance with Legislative Decree no. 22 of 2 February 2007, as amended and supplemented and therefore must:

The conversion device and related communication protocol must comply with UNI TS 11629.

Mains-powered conversion devices must comply with the requirements of UNI TS 9167-3. In the event of a power failure, an alternative power supply must be provided to ensure the operation of the measurement system for a duration of > 6h.

The gas volume conversion device, in addition to the specifications of the following paragraphs, must be supplied Class 2, complying with UNI-TS 11629 and UNI-EN 12405-1. The electronic gas volume conversion device must also be able to receive from the quality analyser/gas chromatograph (please refer to the reference specification) the gas quality values including PCS for conversion operations (according to the calculation algorithm implemented). In this regard, the Class 2 electronic gas volume conversion devices must check the availability of quality data from the QS apparatus (Gas Chromatograph or Quality Analyser) at least every 2 min.

The electronic volume conversion device must be capable of acquiring pulses from both conventional meters (NCVNon Contact Voltage) and ultrasound meters ("OC" or Namur non-electrically isolated passive output).

The electronic gas volume conversion device must be suitable for the conversion of gas volumes on volumetric measurement systems.

In addition, in order to allow connection to the transporter's acquisition system, the serial port must have the compatible POT communication protocol.

## TECHNICAL CHARACTERISTICS OF THE TYPE 1 GAS VOLUME CONVERSION DEVICE

The gas volume conversion device must meet the following requirements (detailed features to be specified by the Supplier in the documentation accompanying the product):

- convert gas volumes, measured by ultrasound (ref T.S. 9995305 Ed2) or turbine gas meters (ref. T.S. 2401301) from operating conditions (Vm) to standard conditions (Vb) according to the calculation algorithm defined in the AGA REPORT #7;

- type of conversion device according to UNI EN 12405-1: "Type 1", in which the sensors (temperature and pressure) are an integral part of the same;

- degree of protection of the housing: at least IP 65 according to CEI EN 60529 (CEI 70-1) and at least IK 09 according to CEI EN 62262 (CEI 70-4);

- classification:

- mechanical environment: class M2 (see UNI EN 12405-1, point 3.3.1);

- electromagnetic environment: class E2 (see UNI EN 12405-1, point 3.3.2);

- environmental conditions:

- ambient operating temperature (minimum range): - 25 °C ÷ + 55 °C (see UNI EN 12405-1, point 5.2.1);

- relative humidity: condensed humidity, range at least 10% ÷ 93% (see UNI EN 12405-1, point 5.2.2);

- max. power supply at 12 VDC  10%; the devices must be able to operate with a back-up battery for more than 6h with 1-minute hourly communication via the communication port with, for example, the RIU device;

- temperature probe: consisting of a platinum resistance thermometer (thermoresistance) PT 1000/PT 100, tolerance class A, four-wire configuration, conforms to CEI EN 60751. Measurement range -20 °C ÷ +70 °C. Suitable for installation in a thermowell, with the following features: male threaded connection ND ¾" ANSI B.2.1. NPT, with a diameter of 6 mm and a length of 65 mm; the supply of the thermowell must also be envisaged on explicit request;

- pressure transducer with scale range 0 ÷ 10 bar, 0 ÷ 6 bar or 0 ÷ 2 bar absolute, accuracy class ± 0.3 % of measured value or better, maximum transient overpressure ≥ 200 % of upper scale range value; suitable for connection to a pressure intake, with threaded gas connection ND ¼" male;

- maximum overall dimensions (length x height x depth): 240 mm x 220 mm x 100 mm, with a tolerance of ± 20 mm per dimension;

- category according to directive 2014/34/EU (ATEX): at least 2G IIA T3, suitable for installation in explosion hazard locations classified as "zone 1" according to CEI EN 60079-10-1 (CEI 31-87). The equipment is part of an intrinsically safe system and must be manufactured according to CEI EN 60079-25. Graphic LCD display, which lights up automatically whenever any key on the keyboard is pressed, for data display;

- mounting: wall or, by means of a bracket, on a ND 2" post;

- serial port for communication with the remote power supply module located in a safe area, through which it also acquires data from the QS;

- additional optical communication ports on which data can be downloaded via portable devices, configuration/maintenance operations can be performed via external devices, etc.;

- designed for intrinsically safe connection with field transmitters i.e. high and/or low frequency (HF-LF) pulse signals according to those generated by the reference gas meter;

- static type memory (e.g. Compact Flash, SD card or similar) which must contain events, hourly, daily and monthly data and which must be store at least the cubic metres at operating conditions and at reference conditions, the energy (when calculated) the maximum and minimum flow rates (daily) and period diagnostics, with an update interval of the static memory on a new event of not more than 15 min, and rewriting of the memory in cyclic mode, with data extraction by copying (fully automatically managed) the entire memory onto a portable medium;

- alarm signals for Calculator Fault (CF), Calculator mains failure (CMF), Calculator battery low (CB), out-of-scale inputs, etc., for remote re-transmission of such alarms;

- software of the electronic gas volume conversion device in accordance with the requirements of WELMEC 7.2: Software Guide (MID).

Moreover, the execution criteria for electrical wiring must comply with the current state-of-the-art WRMPs (Ex-i protection method).

In gas measurement systems where the Client states the need for the installation of a second volume converter, it reserves the right to consider the possibility of supplying dual-channel volume converters, instruments capable of simultaneously acquiring pulses, pressure, temperature from two different measurement lines and simultaneously processing the volumes.

The solutions indicated must be quoted at the tender stage.

## REMOTE POWER SUPPLY MODULE

The remote power supply module must meet the following requirements (detailed characteristics to be specified by the Supplier in the documentation accompanying the product):

- power supply 12 VDC  10%; coming from the power supply unit; Positioning to be provided in "non-explosion hazard area" according to CEI EN 60079-10-1 (CEI 31-87); the remote reading module must be certified according to Directive 2014/34/EU (ATEX) as "associated equipment", therefore suitable for connection to the conversion device mentioned in point 6.1 above;

- degree of protection of the housing: at least IP 65 according to CEI EN 60529 (CEI 70-1) and at least IK 09 according to CEI EN 62262 (CEI 70-4);

- operating temperature: minimum range -25 °C ÷ +55 °C;

- maximum overall dimensions (length x height x depth): 240 mm x 220 mm x 100 mm, with a tolerance of ± 20 mm per dimension;

- outputs for signal repetition:

- at least two configurable for pulse repetition of nominal and corrected volumes (cubic metres and cubic metres at standard conditions) or configurable as digital for alarm signalling (no mains, low battery, etc.);

- at least one analogue 4 ÷ 20 mA;

- RS-232/485 serial port implementing the MODBUS RTU/ASCII protocol, programmable for interfacing with gas chromatograph/gas quality analyser;

- RS-485 serial port implementing the POT Protocol for interfacing with the transporter’s RIU;

- RS232 serial port for communication with type 1 converter located in ATEX classified zone;

- the Client reserves the right to request that an additional RS-485 serial port be provided with MODBUS RTU protocol and with metrological certification for connection to the relative ultrasound meter; the converter will therefore be able to use the input data to calculate the volumes in transit; it must also be possible to acquire the diagnostic values (e.g. metrological and non-metrological alarms/errors) that may be transmitted by the meter and made available on appropriate MODBUS registers in read-only mode for Italgas RTU 104;

- additional optical communication ports on which data can be downloaded via portable devices, configuration/maintenance operations can be performed via external devices, etc.;

- volume converter type 1 power supply in ATEX classified area;

- mounting: wall or, by means of a bracket, on a ND 2" post;

- provision of an additional RS-485 or Ethernet serial interface port supporting MODBUS RTU or MODBUSTCP communication protocols for connection to the Italgas RTU locally and for the transfer of all data processed;

- must be equipped with an additional RS-485 serial interface port with POT protocol for local connection with an Italgas RIU to transfer all processed data to the IoT platform;

- 4G/2G industrial modem/router (see point 5.4.1), as a minimum Dual-band (900-1800 MHz) for POT and Old (formerly Snam) protocol communication, which must have at least the following main characteristics:

- suitable for use in DATA applications;

- support the function for receiving telephone calls in CSD data mode;

- state-of-the-art integrated circuits that offer high standards of energy efficiency;

- remote antenna and connection cable included in the supply;

- SIM card reader at the following operating voltages 5V, 3V and 1.8V according to ISO/IEC 7816-3.

Below is a summary of the required ports:

| Port type | Communication Protocol | Number | Mandatory |
| --- | --- | --- | --- |
| RS232 | serial | 1 | YES |
| RS 485 | POT | 2 | YES |
| RS 485 | MODBUS | 1 | YES |
| RS 485/ethernet | MODBUS | 1 | YES |
| RS 485 | MODBUS (Metrological) | 1 | NO (on request) |

## CONNECTION CABLES

### Input signals and connection to the remote reading module

Multicore cable for fixed laying, with flexible conductors, made of annealed red copper (class 5 according to CEI EN 60228). High-modulus ethylene propylene rubber (HEPR) core insulation or equivalent, according to CEI EN 50363-0 and CEI EN 50363-1. Outer sheath of PVC quality Rz/TM 2 or equivalent, in accordance with CEI EN 50363-0 and CEI EN 50363-4-1, light blue (RAL 5015); other colours, e.g. light grey (RAL 7035), are only permitted on specific request. "Total shielding" consisting of aluminium/polyester tape (protection from electrostatic interference) and copper braid (protection from electromagnetic interference), or equivalent. (For further details, see T.S. IE-1/501 point 4.5).

Main indicative parameters:

- Length of connection cable to the remote reading module: at least 4 m (compatible with the characteristics of the intrinsically safe system);

- Number of conductors and length of connection cable to signal sensors to be defined depending on the type of transducers used;

- Rated voltage Uo/U: ≥ 450/750 V;

- Diameter of individual conductors: ≥ 0.1 mm;

- Conductor cross-section: 0.5 ÷ 1 mm2.

General properties:

- Suitable for systems built in accordance with CEI EN 60079-14 (CEI 31-33) and CEI EN 60079-25 (CEI 31-79);

- Fire-retardant in accordance with CEI 20-22/0;

- Provided with IMQ or equivalent approval.

It should be noted that the pressure and temperature probes must be installed on the meter, the connection cables with the sensors are solely for sending data to the converter. Connections bringing gas to the converter for measurement of the necessary parameters are not allowed.

### Earthing

Single-core cable for fixed laying, with flexible conductors, made of annealed red copper (class 5 according to CEI EN 60228). PVC insulation of R2 quality or equivalent, according to CEI EN 50363-0 and CEI EN 50363-4-1, yellow-green. Complete with cable lugs at brass ends. (For further details, see T.S. IE-1/501, point 4.4.1).

Main indicative parameters:

- Rated voltage Uo/U: ≥ 450/750 V;

- Section: ≥ 4 mm2;

- Length: ≥ 2 m.

General properties:

- Fire-retardant in accordance with CEI 20-22/0;

- Provided with IMQ or equivalent approval.

# TECHNICAL CHARACTERISTICS data LOGGER

The data logger device according to the provisions of UNI 9167-3 must, to all intents and purposes, be a Class 1 type 1 converter that must comply with UNI EN 12405-1, UNI EN ISO 12213-1/2 or UNI EN ISO 12213-3 in accordance with Legislative Decree no. 22 of 2 February 2007, as amended and supplemented, and must therefore:

- comply with UNI TS 11629 and UNI EN 12405-1;

- if mains-powered, comply with the provisions of UNI TS 9167-3. In the event of a power failure, it must guarantee an autonomy of at least 15 days;

- be able to acquire pulses both from conventional meters (NCVNon Contact Voltage) and from ultrasound meters (non-electrically isolated passive output "OC" or Namur) having a max. frequency of 2Hz and a duration of ≥200ms.

## DATA LOGGER ELECTRONIC BACK-UP DEVICE (FF TYPE 1)

The data-logger must meet the following requirements (detailed characteristics to be specified by the Supplier in the documentation accompanying the product):

- convert gas volumes, measured by ultrasound (ref T.S. 9995305 Ed2) or turbine gas meters (ref. T.S. 2401301) from operating conditions (Vm) to standard conditions (Vb) according to the calculation algorithm defined in the AGA REPORT #7;

- type of conversion device according to UNI EN 12405-1: "Type 1", in which the sensors (temperature and pressure) are an integral part of the same;

- degree of protection of the housing: at least IP 65 according to CEI EN 60529 (CEI 70-1) and at least IK 09 according to CEI EN 62262 (CEI 70-4);

- classification:

- mechanical environment: class M2 (see UNI EN 12405-1, point 3.3.1);

- electromagnetic environment: class E2 (see UNI EN 12405-1, point 3.3.2).

- environmental conditions:

- ambient operating temperature (minimum range): - 25 °C ÷ + 55 °C (see UNI EN 12405-1, point 5.2.1);

- relative humidity: condensed humidity, range at least 10% ÷ 93% (see UNI EN 12405-1, point 5.2.2).

- max. power supply at 12 VDC  10%; the devices must be able to operate with a back-up battery for a period of more than 15 days;

- temperature probe: consisting of a platinum resistance thermometer (thermoresistance) PT 1000/PT 100, tolerance class A, four-wire configuration, conforms to CEI EN 60751. Measurement range -20 °C ÷ +70 °C. Suitable for installation in a thermowell, with the following features: male threaded connection ND ¾" ANSI B.2.1. NPT, 6 mm in diameter and 65 mm long. The supply of the thermowell must also be envisaged on explicit request;

- pressure transducer with scale range 0 ÷ 10 bar, 0 ÷ 6 bar or 0 ÷ 2 bar absolute, accuracy class ± 0.3% of measured value or better, maximum transient overpressure ≥ 200% of upper scale range value; suitable for connection to a pressure intake, with threaded gas connection ND ¼" male;

- maximum overall dimensions (length x height x depth): 240 mm x 220 mm x 100 mm, with a tolerance of ± 20 mm per dimension;

- category according to directive 2014/34/EU (ATEX): at least 2G IIA T3, suitable for installation in explosion hazard locations classified as "zone 1" according to CEI EN 60079-10-1 (CEI 31-87). The equipment is part of an intrinsically safe system and must be manufactured according to CEI EN 60079-25;

- graphic LCD display, which lights up automatically whenever any key on the keyboard is pressed, for data display;

- mounting: wall or, by means of a bracket, on a ND 2" post;

- serial port for communication with the remote power supply module located in a safe area;

- additional optical communication ports on which data can be downloaded via portable devices, configuration/maintenance operations can be performed via external devices, etc.;

- designed for intrinsically safe connection with field transmitters i.e. a low frequency (LF) pulse signals according to those generated by the reference gas meter;

- static type memory (e.g. Compact Flash, SD card or similar) which must contain events, hourly, daily and monthly data and which must be store at least the cubic metres at operating conditions and at reference conditions, the energy (when calculated) the maximum and minimum flow rates (daily) and period diagnostics, with an update interval of the static memory on a new event of not more than 15 min, and rewriting of the memory in cyclic mode, with data extraction by copying (fully automatically managed) the entire memory onto a portable medium;

- alarm signals for Calculator Fault (CF), Calculator mains failure (CMF), Calculator battery low (CB), out-of-scale inputs, etc., for remote re-transmission of such alarms;

- software of the electronic gas volume conversion device in accordance with the requirements of WELMEC 7.2: Software Guide (MID).

Moreover, the execution criteria for electrical wiring must comply with the current state-of-the-art WRMPs (Ex-i protection method).

## REMOTE POWER SUPPLY MODULE

The remote power supply module must meet all the requirements (detailed characteristics to be specified by the Supplier in the documentation accompanying the product) set out in point 6.2 above, with the only exceptions of the RS232/485 programmable serial port for interfacing with the gas chromatograph/gas quality analyser, as the device will NOT be connected to the QS , and of the RS-485 serial port or Ethernet supporting MODBUS RTU or MODBUS TCP communication protocols for connection with the Italgas RTU, as this is not envisaged on the data logger.

## CONNECTION CABLES

### Input signals and connection to the remote reading module

Multicore cable for fixed laying, with flexible conductors, made of annealed red copper (class 5 according to CEI EN 60228). High-modulus ethylene propylene rubber (HEPR) core insulation or equivalent, according to CEI EN 50363-0 and CEI EN 50363-1. Outer sheath of PVC quality Rz/TM 2 or equivalent, in accordance with CEI EN 50363-0 and CEI EN 50363-4-1, light blue (RAL 5015); other colours, e.g. light grey (RAL 7035) are only permitted on specific request. "Total shielding" consisting of aluminium/polyester tape (protection from electrostatic interference) and copper braid (protection from electromagnetic interference), or equivalent. (For further details, see T.S. IE-1/501, point 4.5)

Main indicative parameters:

- Length of connection cable to the remote reading module: at least 4 m (compatible with the characteristics of the intrinsically safe system);

- Number of conductors and length of connection cable to signal sensors to be defined depending on the type of transducers used;

- Rated voltage Uo/U: ≥ 450/750 V;

- Diameter of individual conductors: ≥ 0.1 mm;

- Conductor cross-section: 0.5 ÷ 1 mm2.

General properties:

- Suitable for systems built in accordance with CEI EN 60079-14 (CEI 31-33) and CEI EN 60079-25 (CEI 31-79);

- Fire-retardant in accordance with CEI 20-22/0;

- Provided with IMQ or equivalent approval.

It should be noted that the pressure and temperature probes must be installed on the meter, the connection cables with the sensors are solely for sending data to the converter. Connections bringing gas to the converter for measurement of the necessary parameters are not allowed.

### Earthing

Single-core cable for fixed laying, with flexible conductors, made of annealed red copper (class 5 according to CEI EN 60228). PVC insulation of R2 quality or equivalent, according to CEI EN 50363-0 and CEI EN 50363-4-1, yellow-green. Complete with cable lugs at brass ends. (For further details, see T.S. IE-1/501, point 4.4.1)

Main indicative parameters:

- Rated voltage Uo/U: ≥ 450/750 V;

- Section: ≥ 4 mm2;

- Length: ≥ 2 m.

General properties:

- Fire-retardant in accordance with CEI 20-22/0;

- Provided with IMQ or equivalent approval.

# POWER SUPPLY UNIT for Chapter 6 and 7 devices only

The power supply unit must comply with CEI 22-32, CEI 103-1/11 and the following requirements (detailed characteristics to be specified by the Supplier in the documentation accompanying the product):

- be suitable for mains supply voltage 230 VAC ±15% at 50 Hz ±5%;

- have electrical protections sized and aligned on all input and output circuits;

- protection against line surges - on the supply side - with protective devices (SPDs) complying with T.S. TC-1/706;

- filter to prevent the emission of radio interference in accordance with CEI 303-13;

- provide levelling filters against residual waves and ripple, complete with polarity reversal protection and inserted on each DC output;

- provide stabilised power supply switching filtered with the above-mentioned filters, which must be able to supply both the remote supply circuit of the data-logger, the type 1 converter and the ultrasound meter (if present) these external supplies must not create an overload or compromise the performance of the system in any way;

- provide programmable thresholds for signalling excessive, insufficient  or absent mains supply voltage with voltage-free NA type contacts for remote re-transmission of generated signals;

- run a periodic automatic battery test to check that the batteries are actually present and ready to take over in the event of a primary power failure without interrupting the power supply. If the test is failed, it must generate battery alarm information via voltage-free NC-type contacts;

- provide appropriately sized back-up batteries to ensure the autonomy of all connected equipment, in accordance with UNI 9167-3 and UNI/TS 11692.

The power supply unit must be housed in a cabinet made of either polyester or powder-coated metal and must have the following features:

- tamper-resistant security lock;

- frontal access;

- access door to live parts fitted with special locking device (e.g. hexagon socket spanner);

- cable entry possible from the bottom, which can be completed with pipe fittings or cable glands;

- protection against direct contacts in accordance with CEI 64-8;

- degree of protection according to CEI EN 60529 (CEI 70-1), not less than IP43 for indoor installations and not less than IP65 for outdoor installations;

- degree of protection against external mechanical impact (IK code) according to CEI EN 62262 (CEI 70-4), not less than IK07.

Input/output terminal blocks, and wiring in general, must be appropriately marked, protected against accidental contact and easily accessible, in accordance with the specific product standards and CEI 64-8.

Safety signs must comply with the relevant provisions of Title V of Legislative Decree 81/08 as amended and supplemented.

Italgas Reti is entitled to request, at the purchase stage, that by means of differentiated input, the necessary energy be obtained from photovoltaic panels with relative batteries. The sizing of such an alternative power supply unit shall be carried out exclusively on the basis of precise technical specifications produced by the Supplier of the equipment, who shall assume overall responsibility for the same.

The remote power supplies of the data-logger and the type 1 converter (if present) must be installed inside the same cabinet as contains the power supply unit; special attention must be paid to protection against direct and indirect contacts by insulating the 230 VAC power supply circuits with suitable shields and suitably spacing/separating the IS circuits.

# Security of electronic devices

The devices described in the previous chapters must provide for an anti-tamper or anti-fraud system for parts or components, where not already provided for by the standard. It will be up to the Client to assess the effectiveness of such solutions. These devices must also meet the following requirements:

- prevent a copy of the firmware from being obtained through physical access to the device and main components;

- disable, where possible, any UART, JTAG and SWD interfaces on the final product;

- protect the SoC's internal and external RAM and flash memories (if present) with appropriate read/write access protection bits;

- where not provided, the pin for the anti-tampering switch must be hidden and not accessible from the outside;

- where possible, only use chips with a BGA package so as to make access to the component pins difficult and to hide the communication tracks between the main components, such as SoCs, external flash memories and modems inside the PCB wafers;

- in any case, suitably protect (with protective resins) all major electronic components (e.g. flash memory, modem chips, etc.) in order to make access more difficult;

- where possible, on the finished product remove/hide silk-screened and identification codes of individual components;

- use mechanisms to verify the authenticity of the firmware, such as secure boot;

- where not provided, use mechanisms capable of securely storing (e.g. Secure Storage/Secure Element) the cryptographic material and credentials used by the device such as the encryption keys;

- where not provided, use "secure components", i.e. hardware chips that are used to implement secure boot/storage, or alternatively obfuscation algorithms to protect security parameters/credentials;

- provide any other system which in the opinion of the designer should be made available to protect parts or components.

# Technical assessment

In relation to Legislative Decree 81/08, as amended and supplemented, Italgas Reti reserves the right, in its evaluation of the use of the proposed products, to consider the operational consequences deriving from the conditions of use of the equipment as prescribed by the Supplier in the "Use and Maintenance Manual".

# Marking

The products covered by this T.S. must be provided with the markings required by the EU Directives and by the relevant applicable technical standards (such as UNI EN 12405-1, CEI EN 60079-0, CEI EN 60079-11, CEI EN 61000, CEI EN 61326-1, etc.), considering that the affixing of the CE marking, together with any other markings that may be used, is subject to the provisions of Decision no. 768/2008/EC of 9 July 2008 on a common framework for the marketing of products, implemented by the legislative decrees transposing the applicable product directives, a non-exhaustive list of which is given under "Reference Standards" in this T.S.

They must therefore bear the conformity  marking, affixed in the manner provided for by the legal provisions in force, together with any other markings provided for by the same directives (e.g. "Additional metrology marking” according to the MID Directive, "specific marking of explosion protection”  in accordance with the ATEX Directive, “marking relating to the disposal of electrical and electronic equipment -  in accordance with the WEEE Directive, etc.).

# TYPE TEST

In the design phase of the automated measurement system, the "Type Tests" required by the Reference Standards and/or the Supplier's design standards and by the standards referred to therein, for verifying the intended end use of the product must have been performed.

DOCUMENTATION REQUIRED FROM THE SUPPLIER

## Supplier

The potential Supplier must be qualified as an Italgas Supplier.

## Documents to be submitted

The potential Supplier must submit the following documentation to the PROMA-CMMAT Department at the tender stage:

- “Declaration of Conformity” with this technical specification and any specific documents mentioned in it (legislative provisions, applied standards, etc.) to which the Supplier refers for the design and construction of the product, in accordance with the requirements of UNI CEI EN ISO/IEC 17050-1 (see the example in APPENDIX 1 to this T.S.);

- Whatever else the potential Supplier considers useful to better qualify the proposed product.

## Test Documentation

The Supplier must issue a “type 3.1” Inspection Certificate in accordance with UNI EN 10204, which states that the products provided are compliant with the requirements of these specifications and which provides the test results.

Registration of the full production/test documentation completed by the Supplier must be kept, on the basis of legal provisions. for 10 years under its responsibility, and must be made available whenever requested by the Client.

## Supply Documentation

The following documentation is required from the Supplier when supplying the automated measurement system:

- "EU Declaration of Conformity" in accordance with the Legislative decrees implementing the Directives applicable to all the components of the measurement system (e.g. BT, ATEX, RED, EMC, MID, WEEE, RoHS II etc.);

- copy of the "Installation, Use and Maintenance Manual" (in Italian) for the correct use of the product;

- descriptive document of the intrinsically safe system providing an adequate analysis of the level of safety achieved by the system;

- MID certification (directive 2014/32/EU);

- documents compliant with Legislative Decree no. 286 of 21 November 2005, as amended;

- any other technical documents and/or drawings requested by the relevant Italgas Reti departments.

# TESTS AND INSPECTIONS

Italgas Reti reserves the right:

- To be present with its own Inspectors and/or Inspection Companies appointed by the same to carry out tests/checks at the production plant and at the Supplier's care and expense, to check the constructive and functional compliance of the materials in accordance with the specifications and/or reference standards;

- to verify, upon receipt and/or under actual conditions of use, the perfect compliance of the goods with the functional technical characteristics expressly indicated in the Contract.

It is understood that the favourable outcome of our inspection and checking of the materials shall not release you in any way from the responsibilities and obligations arising from each individual contract.

The devices described in the preceding chapters, if used in legal metrology, after their commissioning, shall be subject to subsequent checks, i.e. "periodic verification" (legal periodic metrological control) at the frequency defined according to the type or following repair for any reason whatsoever, involving removal of labels or other seal including of an electronic type and "random metrological checks" intended to ascertain their proper functioning and use pursuant to Ministerial Decree no. 93 of 21 April 2017, as amended and supplemented.

## Right of the Client

In order to verify the conformity of the proposed products with the contents of this technical specification and the cited standards to which reference is made, it is Italgas Reti's right, for each purchase order, to request from the Supplier:

- the production of further relevant technical and/or graphic documentation with the indicated characteristics;

- the performance of any additional laboratory and/or field tests in relation to the required product characteristics.

# CONDITIONS OF SUPPLY

Supplier's Standard in compliance with Legislative Decree no. 152 of 3 April 2006 as amended and supplemented.

# PRODUCT WARRANTY

The metrological performance and construction characteristics of the electronic gas volume conversion device must be guaranteed for 3 years under normal use. The warranty shall apply if the performance deviation can be attributed to a defect in the electronic gas volume conversion device ex works.

All electronic gas volume conversion devices that for any reason (periodic, random) have been inspected with a negative outcome must be replaced under warranty, on the basis of the warranty terms set out above.

# REFERENCE STANDARDS

- Legislative Decree no. 22 of 02 February 2007, as amended. - "Implementation of Directive 2004/22/EC on measuring equipment and Directive 2014/32/EU of 26 February 2014 as amended by the delegate directive (EU) 2015/13 of 31 October 2014 on the harmonisation of the laws of the Member States relating to the making available on the market of measuring equipment (recast), providing for its repeal".;

- Legislative Decree no. 128 of 22 June 2016 – "Implementation of Directive 2014/53/EU on the harmonisation of the laws of Member States relating to the making available on the market of radio equipment, repealing Directive 1999/5/EC”;

- Legislative Decree no. 27 of 04 March 2014, as amended. - 'Implementation of Directive 2011/65/EU on the restriction of the use of certain hazardous substances in electrical and electronic equipment';

- Legislative Decree no. 81 of 09 April 2008, as amended. - “Implementation of Article 1 of Law no. 123 of 3 August 2007 on the protection of health and safety in the workplace”;

- Legislative Decree no. 152 of 03 April 2006, as amended. - “Environmental standards”;

- Legislative Decree no. 286 of 21 November 2005, as amended. - “Provisions for the regulatory reorganisation of the regulated liberalisation of the road haulage business”;

- Ministerial Decree no. 220 of 28/05/1988 – "Implementation of Directive no. 86/361/EEC on the initial stage of mutual recognition of type approval of telecommunications terminal equipment”;

- Decree no. 93 of 21 April 2017 as amended and supplemented – "Regulations on the implementation of legislation on the control of measurement instruments in service and the supervision of measurement instruments in compliance with national and European regulations";

- CEI EN IEC 60079-0 (CEI 31-70) - “Explosive atmospheres - Part 0: Equipment - General Requirements";

- CEI EN 60079-11 (CEI 31-78) “Explosive atmospheres - Part 11: Equipment with intrinsically safe protection mode "i"";

- CEI EN 60079-25 (CEI 31-79) “Explosive atmospheres - Part 25: Intrinsically safe electrical systems';

- CEI EN 60079-10-1 (CEI 31-87) “Explosive atmospheres - Part 10-1: Classification of areas – Explosive gas atmospheres";

- CEI EN 60079-14 (CEI 31-33) “Explosive atmospheres - Part 14: Design, selection and installation of electrical systems;

- CEI 31-108 – Explosive atmospheres – Guide to the design, selection and installation of electrical systems in application of standard CEI EN 60079-14 (CEI 31- 33):2015-04;

- CEI EN 60529 (IEC 70-1) - 'Degrees of protection provided by enclosures (IP Code)';

- CEI EN 62262 (CEI 70-4) – "Degrees of protection provided by enclosures of electrical equipment against external mechanical impacts (IK Code)";

- CEI EN 62208 (CEI 17-87) – "Empty enclosures for low-voltage switchgear and controlgear assemblies – General requirements";

- CEI EN 61439-1 (CEI 17-113) – "Low-voltage switchgear and controlgear assemblies (LV panels)";

- CEI EN 62040 – "Uninterruptible power systems (UPS)";

- CEI EN 60947 – "Low Voltage Equipment";

- CEI 20-38 – "Halogen-free, rubber-insulated, fire retardant cables for rated voltages U0/U not exceeding 0.6/1 kV";

- CEI EN 60445 (CEI 16-2) – "Basic and safety principles for man-machine interface, marking and identification – Identification of equipment terminals and conductor ends";

- CEI 103-1/11 – "Internal telephone systems – Part 11: Power supply";

- CEI EN IEC 61558-1 (CEI 96-3) – "Safety of transformers, reactors, power supply units and combinations thereof. Part 1: General requirements and tests";

- CEI 303-13 – "Telephone terminals, special telephone terminals and user auxiliary devices";

- CEI EN 61000 – "Electromagnetic compatibility (EMC)";

- CEI EN 60068 – "Environmental testing";

- CEI EN 61326-1 – "Electrical equipment for measurement, control and laboratory use - EMC requirements - Part 1: General Requirements";

- UNI EN 12150 – "Glass in building - Thermally toughened soda lime silicate safety glass";

- UNI EN 12405-1 – "Gas meters. Conversion devices. Part 1: Volume conversion";

- UNI EN ISO 12213-1 – "Natural gas - Calculation of the compression factor - Part 1: Introduction and Guidelines";

- UNI EN ISO 12213-2 – "Natural gas - Calculation of the compression factor - Part 2: Calculation using molar composition analysis";

- UNI EN ISO 12213-3 – "Natural gas - Calculation of the compression factor - Part 3: Calculation using physical properties";

- AGA REPORT #7 – "Measurement of Natural Gas by Turbine Meters (2006) - XQ0601";

- UNI 9167-1 "Gas infrastructures - Pressure control and metering stations for gas connected to transport networks - Part 1: Terms and Definitions";

- UNI 9167-2 "Gas infrastructures - Pressure control and metering stations for gas connected to transport networks - Part 2: Housings, gas pressure control and preheating systems - Design, construction and testing";

- UNI 9167-3 "Gas infrastructures - Pressure control and metering stations for gas connected to transport networks - Part 3: Gas measurement systems - Design, construction and testing";

- UNI EN 14236 – "Domestic ultrasound gas meters";

- UNI EN ISO 5167-1 – "Measurement of fluid flow rate by means of differential pressure devices inserted in solid circular ducts - Part 1: General Principles and Requirements";

- UNI EN ISO 5167-2 – "Measurement of fluid flow rate by means of differential pressure devices inserted in solid circular ducts - Part 2: Diaphragms";

- UNI 11291 – “Gas measurement systems. Hourly-based gas measurement devices";

- ISO/IEC 7816-3 – "Identification cards Integrated circuit cards Part 3: Cards with contacts Electrical interface and transmission protocols";

- UNI CEI EN ISO/IEC 17050-1 - "Conformity assessment - Supplier's declaration of conformity. Part 1: General requirements”;

- WELMEC 7.2: Software Guide (MID);

- UNI/TS 11629 – "Gas measurement systems – Hourly-based gas metering systems directly connected to the transport network";

- Network Code - Snam.

# APPENDICES

- APPENDIX 1 – “Sample declaration of conformity with this technical specification”

- APPENDIX 2 – "Connection pipes for measurement  and remote control systems in standard WRMP"

## APPENDIX 1

Supplier's Declaration of Conformity

(in accordance with the UNI CEI EN lSO/IEC 17050-1 standard)

(1)	No. ...............................................

(2)	Name of the issuer: ..............................................................................................................................................................................

Address of the issuer: .........................................................................................................................................................................

(3)	Subject of the declaration: ...................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

The subject of the above declaration complies with the requirements of the following documents:

Document nos.	Title	Edition/Date of issue

(4)	T.S. TC-1/682	Automated measurement system	Edition 2 of 10/10/2022

Additional information:

(5) 	...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

...................................................................................................................................................................................................................

Signed for and on behalf of:

.............................................................

(Place and date of issue)

(6) 	............................................................. 			......................................................................................................................

(Name and position) 						(Signature or equivalent mark authorised by the issuer)

KEY:

- The Declaration must be issued on headed paper or, if visible, on applied stamps and be uniquely identified (e.g. by a log number);

- The person issuing the Declaration (Supplier) must be unequivocally specified;

- List all the products for which approval for company use is requested (name, type, model), stating any codes assigned by the Supplier itself and, where existing, the relevant material codes assigned by Italgas;

- Include references to the Italgas Reti documents for the proposed products;

- Indicate any deviations from the reference documentation and any other information deemed useful by the Supplier for product evaluation purposes (see note 6) of appendix A of UNI CEI EN ISO/IEC 17050-1);

- Include the handwritten signature of the person authorised to issue the Declaration, stating their full Name, Surname and Position within the Organisation.

## APPENDIX 2

Connection pipes for measurement and remote control systems in standard WRMP

The following shows the connection lines for measurement and remote control systems in standard WRMP 1, 2, 3, 4, 5, 6.

Figure 1: Connection pipes for measurement and remote control systems in standard WRMP 1, 2, 3, 4, 5, 6

Notes:

- The position of the instruments and equipment and the number of connections are purely indicative and must be verified according to design and system requirements;

- Cable installation and protection must be carried out in accordance with CEI EN 60079-14;

- The instrumentation cables must be chosen according to the T.S. IE-1/501 – "Copper cables and cords" and in accordance with applicable standards, and must be verified and validated during the purchase of electronic equipment;

- Instrumentation cables must be installed in cable ducts separate from the other circuits;

- Cable ducts, cable duct accessories and components, fittings, junction boxes, etc. to be used in the WRMP system in intrinsically safe execution must be made of self-extinguishing PVC material and selected in accordance with the T.S. IE-1/751. In addition, cable ducts made of self-extinguishing PVC material must be chosen so as to meet the conditions imposed by standard CEI EN 60079-14 (point 6.5.2) regarding the maximum surface resistance value for insulating pipes, in order to avoid the accumulation of electrostatic charges;

- Particular attention must be paid by the Contractor to the proper execution of the cable routing from the "hazardous location" to the "non-hazardous location" in accordance with CEI EN 60079-10-1. For this purpose, a locking fitting must be used that is mounted (on the "hazardous location" side) on a piece of metal pipe, which must be of sufficient length to ensure that it crosses the entire partition wall between the rooms. It should be "walled-in" with cement material in such a way as to ensure air separation between the rooms. Once the cables have been connected, the joint must be filled with suitable resin to ensure a perfect seal;

- Within the area of the WRMP plant, if provided for in the project, a special duct is built for the connection of the remote control equipment and for the connection of the remote reading system to the public telephone network supply point. The connection is made in a special column located near the cabinets for electrical equipment. To protect the cables, an underground pipe is provided in the section between the column and the electrical room, with inspection manholes in the changes of direction. These manholes are separate from those for the passage of electrical and earth cables, or separated from them by a separating septum of insulating material. Connections to the various equipment are made, inside the electrical room, by means of cable tubes and related accessories and fittings in execution not inferior to IP4X (in accordance with the T.S. IE-1/751), interposing on the lines to the remote control and measurement equipment an additional surge protection to be inserted in a wall-mounted panel, defined in the T.S. TC-1/705, which is generally not included in the supply of the automated measurement system;

- Connections to the various equipment inside the electrical room (non-hazardous location) is made by means of cable tubes and related accessories and fittings in execution not inferior to IP54 (in accordance with the T.S. IE-1/751);

- Ramps for assembling remote control and/or measurement instrumentation must be manufactured in accordance with the prescriptions/indications defined in T.S. TC-1/751;

- Figure 1 shows the connections to a single gas meter considering the supply of an electronic gas volume conversion device in a suitable version to process gas consumption in transit in a single measurement line. For types of WRMP system where there is more than one measurement line, typically the winter and summer measurement lines, the Pt 100 temperature probe or TT temperature transmitter must be moved each time the line is switched over, the electronic gas volume conversion device must be made to detect impulses from the turbine gas meter installed in the appropriate measurement line (by moving the pulse intake) and operate the taps in the manifold tank to have the pressure transmitter PT detect the pressure present in the gas meter in use. This procedure must be carried out by authorised personnel;

- A self-extinguishing PVC junction box must be provided in the vicinity of the gas meter(s) in accordance with T.S. IE-1/751 and with inlet/outlet ports of a size appropriately chosen according to the size of the cables, to be entered and exited with rigid pipes and/or coiled sheaths and relative accessories in self-extinguishing PVC, in accordance with the T.S. IE-1/751 and point 5 of this list;

- A self-extinguishing PVC junction box must be provided in the electrical room in accordance with T.S. IE-1/751 and with inlet/outlet ports entered and exited with rigid pipes and/or coiled sheaths and relative accessories in self-extinguishing PVC, in accordance with the T.S. IE-1/751, of a suitable size and length to reach the measurement cabinet ports defined by the Supplier. The junction box is not shown at Figure 1 in order to avoid confusing the layout of the connection pipes;

- A self-extinguishing PVC junction box must be provided in the electrical room in accordance with T.S. IE-1/751 and with inlet/outlet ports of , a size appropriately chosen according to the size of the cables, to be entered and exited with rigid pipes and relative accessories in self-extinguishing PVC, in accordance with the T.S. IE-1/751, of a suitable size and length to reach the remote control cabinet ports defined by the Supplier. The junction box is not shown at Figure 1 in order to avoid confusing the layout of the connection pipes.

Supplier means the party responsible for the design and construction of the products or its legal representative as defined in Legislative Decree no. 206 of 6 September 2005 as amended and supplemented. - "CONSUMER CODE" pursuant to Article 7 of Law no. 229 of 29 July 2003.

If a cabinet suitable for outdoor installation is requested, then the degree of mechanical protection must be no less than IP 65 and the location must be evaluated during installation, taking into account the classification of explosion hazard locations for the presence of gas in accordance with CEI EN 60079-10-1.

Near the entry and exit points of the cables to and from the field, suitable profiles must be provided for anchoring the cables.

Appropriate cable ducts must be provided for cables coming from the field, dedicated exclusively to the same.

If included in the scope of supply, the printer must be able to receive, manage, store and print all data and information provided by the gas volume conversion device on a continuous roll, and be equipped with a rewinder to keep the paper taut and grouped for printing for at least 2 months.

It must not be possible to change the stored data via the portable medium connection.

The Supplier must specify whether these outputs are active or passive.

The Supplier must indicate at the tender stage the number of serial ports and the specific function.

Programming of the constants by means of a password and user code, and metrological enabling via a sealable key must be possible.

The Client is entitled to request additional digital outputs at the tender stage in accordance with the project requirements.

To solve the equation, the electronic gas volume conversion device also needs the composition of the gas under the two conditions (reference and operating), the density under reference conditions and the size of the measurement line.

If included in the scope of supply, the printer must be able to receive, manage, store and print all data and information provided by the gas volume conversion device on a continuous roll, and be equipped with a rewinder to keep the paper taut and grouped for printing for at least 2 months.

It must not be possible to change the stored data via the portable medium connection.

The Supplier must specify whether these outputs are active or passive.

The Supplier must indicate at the tender stage the number of serial ports and the specific function.

Programming of the constants by means of a password and user code, and metrological enabling via a sealable key must be possible.

The Client is entitled to request additional digital outputs at the tender stage in accordance with the project requirements.

It is the Supplier's responsibility during the purchase stage to indicate the characteristics of the cables and to point out any deviations from the T.S. IE-1/501.

The Client is entitled to request the supply of a connection cable between antenna and 4G modem of a length different from the standard length.

If the conversion device and the remote reading module are integrated in a single module, the maximum permissible overall dimensions are: 320 mm x 250 mm x 100 mm.

It must not be possible to change the stored data via the portable medium connection.

The Client is entitled to request additional digital outputs at the tender stage in accordance with the project requirements.

Intrinsically safe circuits can be "earthed" or "connected to a point of the equipotential system”. The installation method must be chosen in relation to the functional requirements of the circuits and in accordance with the manufacturer's instructions. In intrinsically safe "earthed" systems, protection against electrostatic charges must in any case be ensured, and an earth connection with a resistance between 0.2 MΩ and 1 MΩ (see CEI EN 60079-14, point 16.2.3) fulfils this requirement. This connection must therefore be made, e.g. between the conversion device and a bolt anchoring the cabinet to the base. Alternative solutions may be considered acceptable, provided that they comply with the principles set out in point 16.2.3 of the aforementioned CEI EN 60079-14 and are expressly declared as such by the Supplier in the supporting documentation for the product.

If the conversion device and the remote reading module are integrated in a single module, the maximum permissible overall dimensions are, respectively: 320 mm x 250 mm x 100 mm.

It must not be possible to change the stored data via the portable medium connection.

The Client is entitled to request additional digital outputs at the tender stage in accordance with the project requirements.

Intrinsically safe circuits can be "earthed" or "connected to a point of the equipotential system”. The installation method must be chosen in relation to the functional requirements of the circuits and in accordance with the manufacturer's instructions. In intrinsically safe "earthed" systems, protection against electrostatic charges must in any case be ensured, and an earth connection with a resistance between 0.2 MΩ and 1 MΩ (see CEI EN 60079-14, point 16.2.3) fulfils this requirement. This connection must therefore be made, e.g. between the conversion device and a bolt anchoring the cabinet to the base. Alternative solutions may be considered acceptable, provided that they comply with the principles set out in point 16.2.3 of the aforementioned CEI EN 60079-14 and are expressly declared as such by the Supplier in the supporting documentation for the product.